Per-Unit System

- Introduction

The per-unit system is a widely system of normalization. Being familiar with it is essential to functioning in the world of electric power engineering.

- What is per-unit? (Section 5.5, 5.6)

The per-unit system is a way to transform the numerical quantities (voltages, currents, powers, and impedances) to gain certain advantages while maintaining the basic relations between them (Ohm’s laws).

The main advantage is that voltages tend to be very close to 1.0 and consequently numerical algorithms are more reliable. In addition, the range of values for voltage, currents, powers, and impedances tends to be narrower, offering opportunities to detect bad data.

The basic idea in the per-unit system is that all voltage, currents, powers, and impedances are normalized according to

(1)

In order to remain consistent with Ohm’s laws, we are allowed to choose the base values for any two quantities we want (voltage, current, power, or impedance). Then the other two values must be computed.

For example, it is common to choose the voltage and power bases.

- Voltage base is chosen as nominal voltage

- Power base is chosen as multiple of 10: 1, 10, or 100 kVA or MVA

Then, we compute:

(2)

(3)

The above works for single phase systems or 3-phase systems. In addition, for 3-phase systems, we also have:

(4)

(5)

(6)

(7)

In addition:

(8)

(9)

- Changing base

A calculation that is done very often is to convert a per-unit impedance on one base to a per-unit impedance on another base.

A common situation when this calculation is required is when the purchasing a new piece of equipment (e.g., transformer, generator) from a manufacturer (e.g., ABB, GE, Toshiba, etc.), that has to be modeled in a system (e.g. power flow) study.

The manufacturer will typically supply data in per unit, but on bases that are chosen consistent with the component ratings. These bases are unlikely to be the same as the bases used in the system study.

These formula are easy to derive, by equating the impedance in ohms expressed as a function of the per-unit impedance, e.g.,

(10)

where

,    (11)

Substituting eqs. (11) into (10) and solving for Zpu1 yields

(12)

It may be easier for you to remember it when written in terms of the “new” base (base you are converting to) and the “old” base (base you are converting from):

(13)

It may be the case that only voltage base is changed, or that only power base is changed. The part of eq. (13) that does not get changed will simply be 1.0, and so can be ignored in the expression.

- Perunitization of transmission systems

We will assume our system is “normal” as defined in Section 5.4. This means that the voltage gain for any paralleled transformers is the same.

We will need to per-unitize the data for an entire transmission system. The difficulty here is that, because of transformers, there are different nominal voltages.

The solution to this is to choose the voltage base for one “section” of the system. A section is a set of interconnected components not separated by a transformer.

Then compute the voltage bases for all other sections of the system so that voltage bases of different sections are in the same ratio as the line-to-line voltages.

Let’s work a problem.

Problem 5.19:

Draw an impedance diagram for the system whose one-line diagram is shown in Fig. 1.

Fig. 1

Data for the system is:

G1: 50 MVA, 13.8 kV, X=0.15 pu

G2: 20 MVA, 14.4 kV, X=0.15 pu

M : 20 MVA, 14.4 kV, X=0.15 pu

T1 : 60 MVA, 13.2kV/161kV, X=0.10 pu

T2 : 25 MVA, 13.1kV/161kV, X=0.10 pu

T3 : 25 MVA, 13.2kV/160kV, X=0.10 pu

(I changed voltage rating on LV side of T2 and HV side of T3).

Line 1: 20+80 ohms

Line 2: 10+j40 ohms

Line 3: 10+j40 ohms

Load: 20+j15 MVA at 12.63 kV

We begin by choosing the system power base as S3φ,base=100 MVA.

We must also choose the voltage base in one section of the system. We will select 161kV in Section D.

Now we compute the voltage bases in the other three sections of the system.

Section A:

Section B:

Section C:

Now we can use eq. (13) to convert the given per-unit impedances for G1, G2, M, T1, T2, and T3 into per-unit impedances on our new bases.

G1:

G2:

M:

T1:

T2:

T3:

Note that the last calculation (for T3) could have been done as follows:

Now let’s per-unitize the lines. The line impedances are all in ohms. So we need to find the impedance base for Section D. From eq. (7), we get:

Then we compute

Load:

The load requires a bit of thinking. We are told that it is 20+j15 MVA at 12.63 kV. Now we could convert it to per-unit power by dividing by 100. However, the problem requires that we develop the impedance diagram. So we need to convert this power-specification to an impedance specification.

We can do this because we know the voltage at which the given power is consumed. But one question remains. Since the power is complex, there needs to be an R and an X. But is the R and X in series or in parallel?

We are not given this information and so it is up to us to assume one or the other. We will assume a series combination. In this case,

Now we need to per-unitize it. To do this, we need the impedance base of Section C. This is computed as:

Now we may compute the per-unit impedance as