Use of Tables

- Introduction

We have now the ability to compute inductive reactance and capacitive susceptance of a transmission line given its geometry. To remind you, the most general form of the relevant expressions are:

Inductance (h/m):

- Dm is the GMD between phase positions:

- Rb is the GMR of the bundle

Capacitance (f/m):

- Dm is the same as above.

- is Capacitive GMR for the bundle:

We will review conductor tables because many people still use them and because it provides a good way to review some important and interesting physical properties of conductors that we have not covered and that are not well covered in your book.

- Description of Table A8.1

Table A8.1 on pp 605-607 has 8 columns, with one column, resistance, divided into 4 sub-columns. We describe each one in what follows:

1. Code-word: This is a way of referring to standard conductor sizes that was developed by the Aluminum Association many years ago. They are mostly bird names.

2. Size: The size is designated in kcmil.

What is a cmil (circular-mil)? A cmil is a unit of measure for area and corresponds to the area of a circle having diameter of 1 mil, where 1 mil=10-3 inches, or 1000 mils=1 in.

The area of such a circle is πr2= π(d/2)2, or

π(10-3in /2)2=7.854x10-7 in2.

The area in cmils is defined as the square of the diameter in mils. Therefore:

- 1cmil=(1mil)2 corresponds to a conductor having diameter of 1 mil=10-3 in.

- 1000kcmil=1,000,000cmil=(1000mils)2 corresponds to a conductor having diameter of 1000 mils=1 in.

To determine diameter of conductor in inches, take square root of cmils (to get the diameter in mils) and then divide by 103:

Diameter in inches=.

Example: What is the area in square inches of Conductor Waxwing?

Reference to Table A8.1 indicates it has a size of 266.8 kcmil=266,800 cmils. The diameter in mils is mils. Divide by 1000 to get the diameter in inches to be 0.51653 in. The radius is therefore 0.51653/2=.2583in. The area in square inches is then πr2= π(0.2583)2=0.2095in2.

Noting the ratio 0.2095/266800=0.7854E-6 gives a constant that, when multiplied by the cmils, gives area in square inches [, p. 64]:

Ain2=0.7854E-6*cmil

3. Stranding Al./St.: The most common kind of conductor is Aluminum Conductor Steel Reinforced (ACSR) because it reaps the benefits of aluminum which are

- High conductivity σ (=1/ρ): 61% of σcopper as compared to σbrass which is 25%, σsteel which is 10%, σsilver which is 108%)

- Abundant supply and low cost

- Light

And it reaps the benefit of a few strands of steel, which is increased strength.

A few other kinds of conductors in use are:

- All-Aluminum conductor (AAC)

- All-Aluminum-Alloy Conductor (AAAC)

- Aluminum Conductor Alloy-Reinforced (AAAC)

- Aluminum-Clad Steel Reinforced (Alumoweld)

See below figure [2] for example of ACSR conductor.

Examples:

- Waxwing has Al./St. of 18/1 indicating it has 18 strands of aluminum around 1 strand of steel.

- Partridge has Al./St. of 26/7 indicating it has 26 strands of aluminum around 7 strands of steel.

4. Number of aluminum layers: The strands are configured in a number of concentric layers equal to this number.

Example: The conductor “Flicker” has Al./St. of 24/7. Its core will have 7 strands of steel (6 configured around 1) and 24 strands of aluminum (9 configured around the steel core, 15 configured around the 9).

A general formula for the total number of strands in concentrically stranded cables is

# of strands=3n2-3n+1

where n is the number of layers, including the single center strand [1, p. 64]. The above assumes equal diameters for all strands.

For example, for Waxwing, with n=3 (2 aluminum layers), we have 27-9+1=19, which agrees with Table A8.1 indication that the stranding is 18/1.

5. Resistance: The resistance is given

- for DC at 20°C, and

- for AC (60Hz) at 25, 50, and 75°C.

The DC resistance is computed according to

(1)

where ρ is the resistivity (ohm-meters), l is the conductor length (m), and A is conductor cross-sectional area (m2).

There are three effects which cause the value used in power system studies to differ from RDC:

- Temperature: The resistivity is affected by the temperature and this in turn affects the DC resistance. The influence of temperature on resistivity is captured by the following equation:

(2)

where all values of temperature T are given in degrees centigrade. Parameter α ranges from 0.0034-0.004 for copper and from 0.0032-0.0056 for aluminum and about 0.0029 for steel (see note #2 pg 607)

- Stranding: The effective length is affected by stranding because of spiraling, which tends to increase the DC resistance by about 1 or 2%. So why are conductors stranded instead of being solid []?

- They are easier to manufacture since larger conductors can be obtained by adding successive layers of strands.

- They are more flexible than solid conductors and thus easier to handle, especially in large sizes.

- It reduces skin effect.

- Skin effect: This is from the alternating magnetic field set up by the conductor’s alternating current. The field interacts with the current flow to cause more flow at the periphery of the conductor. This results in nonuniform current density and therefore more losses and higher effective resistance. The increase in resistance from this influence depends only on frequency and conductor material.

6. GMR (ft): With a large number of strands, the calculation of the GMR for a stranded conductor is tedious because we must obtain distances between every combination of strands to compute it, according to:

(see problem 3.7 for an example of this). The availability of this entry in Table A8.1 makes this tedious calculation unnecessary. Note: if you do not have tables, use of r’ instead of Rs is a good approximation (see problem 3.8 for evidence of this).

Consideration of the expression for RS will convince you that Rs will be larger than r’(=dkk), which will cause Rb to be larger, and since Rb goes in the denominator of the logarithm, it will cause the inductance to be smaller. So stranding, like bundling, tends to decrease inductance.

7. Inductive ohms/mile Xa, 1 foot spacing:

This is the per-phase inductive reactance of a three-phase transmission line when the spacing between phase positions is 1 foot. To see why, note that the per-phase reactance in Ω/m of a non-bundled transmission line is 2πfla, where Ω/m. Therefore, we can express the reactance in Ω/mile as

As indicated in the previous #6, Rs may be computed, or we may just use the GMR from the table, so that

Let’s expand the logarithm to get:

which is same as eq. (3.66) in text.

So the values given in the next-to-last column of Table A8.1 are Xa. It is called the inductive reactance at 1 foot spacing because of the “1” in the numerator of the Xa logarithm when GMRtable is given in feet.

Note that to get Xa, you need only to know  the conductor used (we assume f=60 Hz for North America). But you do not need to know the geometry of the phase positions.

But what is Xd? This is called the inductive reactance spacing factor at 60 Hz, and is given by Table A8.2. To get Xd from Table A8.2, you need only to know the GMD between phase positions (again, assume f=60 Hz for North America).

Note that the far left-hand column is the GMD in feet, and, for GMD between 0 and 7 ft, the top row gives additional inches.

8. Capacitive ohms/mile X’a, 1 ft spacing

A similar procedure as above leads us to

X’d is given as the last column in Table A8.1, and X’d is given in Table A8.3.

This is same as eq. (3.69) in text.

Note, however, that Table A8.1 and A8.3 actually give Mega-Ohm/mile, so that you really need to divide the numbers given in the tables by 106 to get ohm/mile (implying that the 106 should really be removed from above equation and units expressed in Mohms/mile to be consistent with the table).

# Endnotes

[] T. Gonen, “Electric Power Transmission System Engineering,” Wiley, 1988.

[] J. Glover and M. Sarma, “Power system analysis and design,” PWS Publishers, 1987