AGC 3

1.0 Introduction

The primary controller response to a load/generation imbalance results in generation adjustment so as to maintain load/generation balance. However, due to droop, it also results in a non-zero steady-state frequency deviation. This frequency deviation must be corrected.

Also, the net scheduled export must be maintained according to the purchase agreements.

Primary control does nothing to correct the steady-state frequency error or the net scheduled export. These two problems are handled by providing a supplementary signal from the control center to each generation unit on automatic generation control (AGC).

The signal is derived from the Area Control Error (ACE) and, when received at a generation plant, activates the “speed changer motor” to adjust the energy supply set point to the generator.

In these notes, we will learn how the ACE is computed, and we will see how it is used in correcting steady-state frequency error.

2.0 Review

From our notes AGC1, we defined the following terms:

- Net Actual Interchange: APij

- Net Scheduled Interchange: SPij

- Interchange Deviation (defined pg 396 of text):

ΔPij=APij-SPij					(1)

Note that the above terms are each defined with respect to two distinct areas.

We also defined, in AGC1, the following terms:

- Actual Export: 				(2)

- Scheduled Export: 			(3)

- Net Deviation: 				(4)

Note that the above three terms are each defined with respect to a single area.

We also saw that the net deviation is related to the net actual and scheduled interchanges, and to the actual and scheduled exports, by:

(5)

Although your text does not define net deviation, it does use it as the first term in the ACE expression of eq. (11.30).

Finally, we saw in our notes AGC2, when discussing the multi-machine case, that

(6)

(7)

If all units have the same per-unit droop constant, i.e., if R1pu=R2pu=…=RKpu, then eqs. (6) and (7) become

(8)

(9)

In eqs. (8) and (9), ΔP represents the change in total load so that it is

- positive if load increases, negative if load decreases;

- positive if gen decreases, negative if gen increases.

3.0 Area Control Error

The Area Control Error (ACE) is composed of

- Net Deviation ΔPi, from eq. (5), written more compactly below:

(5)

When ΔPi>0, it means that the actual export    exceeds the scheduled export, and so the generation in area i should be reduced.

- Steady-state frequency deviation

(10)

When Δf>0, it means the generation in the system exceeds the load and therefore we should reduce generation in the area.

From the above, our first impulse may be to immediately write down the ACE for area i as:

(11a)

Alternatively (and consistent with the text)

(11b)

But we note 2 problems with eq. (11). First, we are adding 2 quantities that have different units. Anytime you come across a relation that adds 2 or more units having different units, beware.

The second problem is that the magnitudes of the two terms in eq. (11) may differ dramatically. If we are working in MW and Hz (or rad/sec), then we may see ΔPi in the 100’s of MW whereas we will see Δf (or Δω) in the hundredths or at most tenths of a Hz. The implication is that the control signal, per eq. (11), will greatly favor the export deviations over the frequency deviations.

Therefore we need to scale one of them. To do so, we define area i frequency characteristic as βi. It has units of MW/Hz. Your text shows (pg. 393) that

(12a)

(12b)

where

- Di is the damping coefficient from the swing equation (and represents the effect of synchronous generator windage and friction);

- DLi is the load damping coefficient and represents the tendency of the load to decrease as frequency decreases (an effect mainly attributed to induction motors).

- The f or ω subscripts indicate whether we will compute ACE using f or ω (text uses ω).

EPRI [] provides an interesting figure which compares frequency sensitivity for motor loads with non-motor loads, shown below in Fig. 0.

Fig. 0

Figure 0 shows that motor loads reduce about 2% for every 1% drop in frequency. If we assume that non-motor loads are unaffected by frequency, a reasonable composite characteristic might be that total load reduces by 1% for every 1% drop in frequency, as indicated by the “total load characteristic” in Fig. 0.

To account for load sensitivity to frequency deviations, we will use parameter DLi according to

(0a)

from which we may write:

(0b)

If our system has a 1% decrease in power for every 1% decrease in frequency, then DLi =1.

The damping terms of eq. (12) are usually significantly smaller than the regulation term, so that a reasonable approximation is that

(12c)

(12d)

Then the ACE equation becomes:

(12e)

(12f)

where Bfi (or Bωi) is the frequency bias characteristic for area i; it is generally set equal to the area i frequency characteristic, βfi (or βωi), as shown in your text on p. 396.

4.0 Example (similar to Ex 11.5 in text)

Consider the two-area interconnection shown in Fig. 1 with data given as below.

Fig. 1

| Area 1 | Area 2 |
| --- | --- |
| Load=20,000 MW | Load=40,000 MW |
| Capacity=20,000 MW | Capacity=42,000 MW |
| Gen=19,000 MW | Gen=41,000 MW |
| R1pu=0.05 | R1pu=0.05 |

The scheduled interchange is 1000 MW flowing from A2 to A1, so that scheduled exports are:

- SP1=-1000 MW

- SP2=1000 MW

There are two parts to this problem:

- Determine frequency and generation of each area and the tie line flow after a 1000 MW loss of load in A1, but before secondary control has taken effect (this means we will determine only the effect of primary control).

- Repeat (1) after secondary control action has taken effect.

Solution:

We assume that area capacities are the ratings:

SR1=20000

SR2=42000

We also note that the load decreases, therefore ΔP=-1000 MW.

- From eq. (8),

Therefore

so that f=60.0484 Hz.

Then we can compute the increase in generation in each area per eq. (9). For Area 1:

Therefore

For Area 2:

Therefore

It is of interest now to obtain the actual exports, and we can do this for each area by taking the difference between load and generation. The loads in areas 1 and 2 were 20000 and 40000, but remember that we lost 1000 MW of load in area 1, so that its value is now 19000. Generation levels were computed above. Therefore

AP1=18,677-19,000=-322.6 MW

AP2=40,322.6-40,000=322.6 MW

So clearly the new tie-line flow is 322.6 MW from A2 to A1.

Note: For multiple areas, calculating tie-line flows requires a power flow solution (DC power flow is suitable to use here).

From eq. (5), net deviation is:

- To find the effect of supplementary control, we first need to compute the frequency bias parameters. We neglect effects of damping terms, so that we use eq. (12c) or (12d):

(12c)

(12d)

But note that the droop constant in (12c) or (12d) is not in per-unit. To convert to per-unit, recall eqs. (13) and (14) from AGC2 notes:

(13a)

(13b)

(14)

Substituting eq. (13a) or (13b) into (14) gives:

(15a)

(15b)

Therefore

(16a)

(16b)

We can use (16a) to calculate the frequency bias term of (12c), which is used in the ACE equation of (12d):

(12d)

Alternatively, we can use (16b) to calculate the frequency bias terms of (12d), which is used in the ACE equation of (12e):

(12e)

In the rest of this example, we will use (16a), (12c), and (12d).

Applying eq. (16a) to obtain Rf1 and Rf2, we get

Then the frequency bias terms are obtained as

Now we can compute the ACE in each area:

So what does this mean?

- ACE1 indicates that the generators in A1 receive a signal to decrease generation by 1000 MW. Recall from page 9 that after primary control action, PM1=18,677.4 MW. With a 1000 MW decrease, then PM1=17,677.4 MW.

- ACE2 indicates that the generators in A2 do not change, so PM2=40,322.6 MW.

But now consider that previous to the secondary control action, we were at a steady state (with steady-state frequency deviation of 0.0484 so that f=60.0484 Hz). Now the ACE signal has caused a decrease in A1 generation by 1000 MW. This action creates a load-generation imbalance of ΔP=+1000 MW that will cause unit primary controllers to act in both areas. From eq. (8):

Therefore

so that f=60.0484 - 0.0484 = 60Hz.

Then we compute the increase in generation in each area per eq. (9). For Area 1:

Therefore

For Area 2:

Therefore

The exports for the two areas will then be:

AP1=18,000-19,000=-1000 MW

AP2=41,000-40,000=+1000 MW

A summary of the situation is given below, where we see that the final control action has resulted in A1 generation entirely compensating for the A1 load decrease of 1000 MW (with area exports unchanged).

| Area 1 | Area 2 |
| --- | --- |
| Load=19,000 MW | Load=40,000 MW |
| Gen=18,000 MW | Gen=41,000 MW |

# Endnotes

[] “Interconnected Power System Dynamics Tutorial,” Electric Power Research Institute EPRI TR-107726, March 1997.