Protection 3

1.0 Introduction

Recall there are five basic classes of relays:

- Magnitude relays

- Directional relays

- Ratio (impedance) relays

- Differential relays

- Pilot relays

We study the directional relay in these notes. This material addresses section 13.2 in your text.

2.0 Directional relays – Tripping Logic

Directional relays have protection zones that include all of the power system situated in only one direction from the relay location. (This is in contrast to magnitude relays which are not directional, i.e., they trip based simply on the magnitude of the relay.)

Consider the one-line diagram in Fig. 1.

Fig. 1

If the relays R1 and R2 in Fig. 1 are directional relays, then

- R1 “looks” to the left but not to the right, and

- R2 “looks” to the right but not to the left.

In order to understand how the directional relay works, first, consider that R2 measures the phasors V2 and I23. Now define the following parameters associated with Fig. 1:

- L23: length of circuit 2-3.

- x: distance from R2 to a fault on circuit 2-3.

- λx=x/L23: the fraction of the circuit length between the relay R2 and the fault at point x.

- I23: the current in circuit 2-3 resulting from the fault x on circuit 2-3 (a phasor).

- V2: the bus 2 voltage (a phasor).

- Z23: total series impedance of circuit 2-3.

If a fault occurs on circuit 2-3, at point x, then the fraction of total circuit length between R2 and the fault is λx. If the circuit has uniform impedance per unit length, then the impedance between the relay R2 and the fault point is λxZ23, and with the bus 2 voltage being V2, the current flowing into circuit 2-3 from bus 2 is:

(1)

But recall that for transmission lines, it is generally the case that R<<X, and therefore

(2)

In that case, eq. (1) becomes:

(3)

Recognizing that 1/j=-90°, eq. (3) becomes:

(4)

Therefore I23 lags V2 by 90°.

Now if the fault occurs on circuit 1-2, at point y in Fig. 1, we can repeat the same analysis as eqs. (1)-(4), except for point y, where we use λy=y/L12,  The result will be

(5)

But R2 measures I23, not I21. Reference to Fig. 1 results in the conclusion that

(6)

Therefore, in this case, I23 leads V2 by 90°.

From this simple analysis, we can establish a logic for the directional relay R1.

Define θ23 as the angle of the phasor I23, i.e.,

(7)

Then if we

- trip when current exceeds pickup AND θ23=-90°

- and block if θ23=+90°,

the relay will be directional.

In reality, of course, the circuits do have resistance, and so eq. (3), for a fault at point x, should be

(8)

And eq. (6), for a fault at point y, should be:

(9)

Relations (8), (9) can be generalized as negative and positive angles, respectively. The current-plane representing the associated relay logic is in Fig. 2:

Fig. 2

The tripping logic can be stated for R2 as

-180<θ23<0, and |I23|>Ip ( Trip

0<θ23<180, or |I23|<Ip ( Block

where Ip is the pickup.

The tripping logic for R1 (which measures I21) would be:

-180<θ21<0, and |I21|>Ip ( Trip

0<θ21<180, or |I21|<Ip ( Block

3.0 Directional relays – when to use them

Consider configurations where current flows from both ends of a circuit during a faulted condition. In such a case, you need breakers at both ends of the circuit because opening only one end will not isolate the fault.

For example, Fig. 3 illustrates a radial configuration having sources at both ends. Figure 4 illustrates a “single-loop” system.

Fig. 3

Fig. 4

One might consider using magnitude relays in these cases so that relays would open if current exceeded the pickup in either direction.

The problem is, however, that the magnitude relays are extremely difficult to coordinate in such configurations.

The following discussion applies to both.

For example, consider relay C. You might think to coordinate it with relay E, assuming that fault current comes from the bus 2 side, so that C is serving as the backup for E.

Based on the coordination approach given in the “Protection 2” notes, we would then set E to operate as fast as possible, for any fault that it sees. Then we would set C to operate more slowly for faults between E and F.

The problem with this scheme is, however, that because E is not directional, and because fault current flows from both ends, E sees faults between breakers C and D. Since E is set to operate as fast as possible, it may operate before D for a fault between C and D, thus unnecessarily de-energizing bus 3. Not cool.

The solution is to use directional relays with the various relays “looking” according to the arrows given in Figs. 5 and 6.

Fig. 5

Fig. 6

Then you would coordinate relays

- A, C, and E together, assuming fault current is sourced only from the direction of relay A, and

- F, D, and B together, assuming fault current is sourced only from the direction of relay F.

4.0 The effects of distributed generation

Today, there is very high interest in the deployment of distributed generation (DG). DG is generation that is located in the distribution system. DG certainly includes rooftop solar, but it also includes other forms of generation, e.g., wind, gas-fired micro-turbines, diesel engines.

A large percentage of distribution load is served by radial feeders, just as we studied in the notes called “Protection2,” and as illustrated in Fig. 7 below.

Fig. 7

Consider, however, the effects of providing a DG at bus 3, as illustrated in Fig. 8.

Fig. 8

When DG is installed on a radial distribution feeder, it is often the case that the feeder is protected by magnitude relays (non-directional overcurrent), but, as Fig. 8 shows, the DG may cause fault current to come from two directions. Therefore, DG installation on a radial feeder may require changes to the protection system so that

- Directional relays are used;

- Coordination for the entire protective system is revised to account for the directional relay characteristics.

I have found some recent IEEE papers that address this issue in some detail. Below are some excerpts from [].

And some excerpts from [].

# Endnotes

[] M. Dewadasa, A. Ghosh, and G. Ledwich, “Protection of distributed generation connected networks with coordination of overcurrent relays,” IECON 2011 - 37th Annual Conference on IEEE Industrial Electronics Society. DOI: 10.1109/IECON.2011.6119434, 2011 , pp. 924-929.

[] D. Jones and J. Kumm, “Future distribution feeder protection using directional overcurrent elements,” IEEE Transactions on Industry Applications, Vol. 50, No. 2, March/April 2014.