## Slide 1: Economic systems for electric power planning Sensitivities
Professor James McCalley

## Slide 2
Operation of the Eastern Interconnection at one time was heavily reliant on using the so-called Interchange Distribution Calculator (IDC), an internet-accessed system that interfaces with OASIS and allows market participants and network operators to efficiently, but approximately, determine the change in MW flow on a flowgate given a set of changes in MW bus injections. OATI is a Minneapolis-based company that has marketed IDC software for many years. The IDC uses sensitivity calculations like we will describe in these notes. These same sensitivities provide another way to implement a DC power flow calculation.
Today the IDC is less central but still used in some situations, see:
https://www.oati.com/solutions/transmission-reliability/congestion-management
OASIS stands for “Open Access Same Time Information Systems.” It focuses on point-to-point (bilateral) transmission service. OASIS sites are used for customers to request transmission services and to designate and terminate network resources and for the transmission providers to post some of the Federal Energy Regulatory Commission (FERC) required postings, such as business practices, transfer capacity, transmission service products and prices. OASIS sites may provide real-time data, e.g., demand forecasts and transmission outage and capacity status. Information about OASIS may be found at the following URLs
www.transmission.xcelenergy.com/Resources/Open-Access-Same-Time-Information-System-&-Open-Access-Transmission-Tariff
https://www.pjm.com/markets-and-operations/etools/oasis.aspx
http://oasis.caiso.com/mrioasis/logon.do
OASIS, IDC, and OATI

## Slide 3
Definitions: SFs and LODFs
Shift factors (SFs) are defined as
They enable efficient calculation of the change of flow on a branch b from a change in injection in bus k, according to a reallocation policy, i.e.,
The line outage distribution factor (LODF) is defined as
dℓ,b = Δfℓ / fk0
It provides the fraction of pre-contingency flow on circuit b that appears on circuit ℓ following outage of circuit b.
Δfℓ = dℓ,b × fk0

## Slide 4
Calculation of SFs
The shift factor and will be denoted by tb,k. It gives the fraction of a change in injection at bus k that appears on branch b. The Power Transfer Distribution Factor (PTDF) is equivalent to the shift factor.
This calculation of shift factors is relatively straightforward based on what we have done using the DC power flow model. Recall the DC power flow equations and the corresponding matrix relation for flows across branches.
(1)
(2)
Inverting eq (1) yields:
(3)
Substitution of (3) into (2) yields:
(4)

## Slide 5
Calculation of SFs
As we have previously defined in the notes on DC PowerFlow:
PB is the vector of branch flows. It has dimension of M x 1. Branches are ordered arbitrarily, but whatever order is chosen must also be used in D and A.
D is an M x M matrix having non-diagonal elements of zeros; the diagonal element in position row k, column k contains the negative of the susceptance of the kth branch.
A is the M x (N-1) node-arc incidence matrix.
B’ is the DC power flow matrix of dimension (N-1)x(N-1), where N is the number of buses in the network, obtained from the Y-bus as follows:
  Replace diagonal element B’kk with the sum of the non-diagonal elements in row k. Alternatively, subtract bk (the shunt term) from Bkk, and multiply by -1.
  Multiply all off-diagonals by -1.
  Remove row 1 and column 1.
P is the vector of nodal injections for buses 2, …, N
The calculation of eq. (4) provides the flows on all lines given the injections at all buses.
But this is not what we want. What we want is the change in flow on all lines given a change in injection at one bus, bus k…
(4)

## Slide 6
Calculation of SFs
So, to be general, let’s assume a change in injection vector ∆P:
(5)
Then, we may compute the change in line flows according to
(6)
Now let the ∆P vector in (5) be all zeros except for the element corresponding to the kth bus, and assign this bus an injection change of 1.

## Slide 7
Calculation of SFs
Our change in injection vector ∆P becomes:
(7)
Then, the change in line flows become
(8)
Question: Does the above equation imply that the injection is changed at only one bus? Explain.
Let’s call this the
“∆P shift vector.”

## Slide 8
Calculation of SFs
So, to be general, let’s assume a ∆P shift vector of:
(7)
Then, the change in line flows become
(8)
Answer: Observe that the ∆P shift vector does not include ∆P1. This is our “slack bus,” and will compensate for the change made at bus k.

## Slide 9
Calculation of SFs
Definition: Recall that the shift factor tb,k is defined as
Then, equation (8) tells us how to compute SFs.
(8)
The “∆P shift vector.”

## Slide 10
Example 1
Consider the example from the LPOPF notes. Compute the shift factors for all branches corresponding to an increase in bus 2 injection (bus k) and a decrease in bus 3 injection (bus j).
The “∆P shift vector.”
The “∆P shift vector.”

## Slide 11
Conceptualization of SFs
You can think of it like this. For a single slack bus, the shift factor for branch b, bus k would be tb,k.
and another shift factor for branch b, bus j would be tb,j.
If we have an injection increase at bus k of ∆Pk and an injection increase at bus j of ∆Pj (negative), then
Increase Pk,
Decrease P1
Decrease Pj,
Increase P1
Then, let ∆Pk=-∆Pj, and we get
(9)
(10)

## Slide 12
Conceptualization of SFs
Then, let ∆Pk=-∆Pj, and we get
(10)
Note that once ∆Pb is obtained, then it must be added to the original flow on branch b to get the resulting total flow following the generation shift, i.e.,
This says that the change in flow on branch b due to a “two-bus shift” of ∆Pk at buses k and j is given by the product of
the differences in single-slack SFs at buses k and j
and the shift ∆Pk.

## Slide 13
SFs for a “distributed slack”
(8)
Equation (8) (on slide 9 and repeated below) shows how to compute the shift factors for the case when a single specified slack bus corresponds to bus 1.
Example 1 (slides 10-12) above shows how to use single slack SFs to compute branch flow changes for a “double shift” of bus k to bus j. This case may be interpreted as a reassignment of the slack from bus 1 to bus j.
What we are interested in now is computation of shift factors for the case when we would like to distribute the slack, or the compensation, throughout the network. The key criterion to guide this is that the elements in the nodal injection vector should correspond to the percentage of desired compensation for each bus, per the next slide.
Matrix B’ is (N-1)x(N-1) as it has bus 1 row & column removed. This makes bus 1 the slack bus, and this row corresponds to bus 2.

## Slide 14
SFs for a “distributed slack”
(11)
where the c-value for bus 1 will be given by
(12)
is the allocation desired for bus 1.
Here, you decide what you want the ci’s to be based on whatever objective you have. Just know that your choice also specifies c1 via eq. (12).

## Slide 15
SFs for a “distributed slack”
One way to distribute the slack is to distribute equally to all buses. In this case,
(13)
where we use N-1 in the denominator because one bus, bus k, is the bus for which the computation is being made (and therefore ck=1). If we use (13), then we can substitute into (12) to obtain:

## Slide 16
Example 2
Using the system from Example 1 above, compute shift factors for all branches corresponding to an increase in bus 2 injection, when the slack is equally distributed to all buses.
Let’s compare shift factors from example 2, when slack is distributed to all buses, to shift factors of example 1, when the slack was distributed to bus 3 only (see slide 10).

## Slide 17
Compare Example 1 and Example 2
Let’s compare shift factors from example 2, when slack is distributed to all buses, to shift factors of example 1, when the slack was distributed to bus 3 only (see slide 10).
Why are they different?
Because reallocation policy is very different! ΔP shift vector is very different.
In example 1, we computed branch flow changes for a unit increase in bus 2 injection and a unit decrease in bus 3 injection.
In example 2, we computed branch flow changes for a unit increase in bus 2 injection and a 0.33 decrease in all other bus injections.
Example 1
Example 2
ΔP shift vector for Example 1
ΔP shift vector for Example 2

## Slide 18
Ways to Distribute the Slack
There are other ways to distribute the slack. For example,
Distribute the slack equally to all generation buses.
Distribute the slack equally to all load buses.
Distribute the slack to all generation buses in proportion to the MVA rating of the generation that is located at the bus (this approach conforms best to reality because it reflects how speed governors work to perform an initial correction to frequency deviation, but this is a topic for EE 457).

## Slide 19
Shift Factor Matrix
Given a specified slack distribution for each of the N buses (these will be called ΔPj), we may compute a matrix of shift factors according to
Here is T-matrix when slack is distributed to bus 1.
Here is T-matrix when slack is distributed to all other buses.
Matrix of ∆P shift vectors.
Matrix of ∆P shift vectors.
When slack is distributed to bus 1, the first column is all zeros and c1=0 which indicates a change at the slack compensated by the slack does nothing.
When slack is distributed to all other buses, the first column is all c=-1/(N-1) and c1=1, which indicates the change is at the slack and it is compensated equally by all other buses, as intended.
Recall:

## Slide 20
Example 3
Let’s compute the T-matrix for Example 2. We assume a distributed slack bus, where, c=-1/3. Therefore
Remember: Each column of the shift factor matrix T is the set of shift factors for a unit increase in injection (generation) at a certain bus. Column 1 is when the injection at bus 1 is increased (there is no “1” in the ∆P shift vector column because that is the one corresponding to the bus that was deleted in the B’ matrix). Column 2 is when the injection at bus 2 is increased, and so on.
Matrix of ∆P shift vectors.

## Slide 21
Example 3
Let’s compute original flows for the system shown below.
The T-matrix was computed on slide 20.
Let’s interpret col 1. Recalling ΔP1 (see slide 19), as given to the left of this comment, we see that col 1 means increase injection at bus 1 and withdraw 0.3333 at all other buses. Then the T-matrix tells us the flows on the five lines will be as indicated to the right.

## Slide 22
Example 3
It is interesting that we get 0 pu additional flow over branches 3 and 4. The reason is due to the symmetry of the network (all branch impedances are the same at Z=j0.1 pu). This symmetry can be most clearly understood by using superposition. Recall our ΔP1 vector.
Begin by applying 0.3333 pu injection at bus 1, -0.3333 pu injection at bus 2, and compute the flows. Then apply 0.3333 pu injection at bus 1, -0.3333 injection at bus 3, and compute the flows. Then apply 0.3333 pu at bus 1, -0.3333 pu injection at bus 4, and compute the flows. Then add the three sets of flows for each branch, and one will observe the exact cancelation of the three flows in branch 3, and the three flows on branch 4.

## Slide 23
A Complete Power Flow Calculation
It is possible to obtain a complete power flow calculation using the shift factors. That is
where ∆Pk is the total injection at bus k.
In this case, however, the shift factors tb,k, defined according to
(14)
must be computed according to the same reallocation policy.
This means that the identity of the bus or buses compensating for the bus k injection change, and the percentages of how much those buses are compensating in injection, must be the same for each column of the T-matrix.
Identifying bus 1 as the single slack satisfies this.
The way we formulated distributed slack does not satisfy this (see next four slides).
I don’t see a way to formulate a distributed slack that satisfies this.
When obtaining a complete power flow calculation using SFs, always use bus 1 as single slack.

## Slide 24
A Complete Power Flow Calculation
We should not compute (14) above using the T-matrix values based on the distributed slack. If we did, for our 4 bus system, each bus’s injection would get distributed differently:
For column 1, "bus k" = bus 1. It means that a 1 unit change at bus 1 gets compensated by a -1/3 unit change at buses 2, 3, 4.
For column 2, "bus k" = bus 2. It means that a 1 unit change at bus 2 gets compensated by a -1/3 unit change at buses 1, 3, 4.
And so on.

## Slide 25
A Complete Power Flow Calculation
This will result in a balanced dispatch (power balance will be satisfied), but it will be a different dispatch than what was intended. As a simple example, try a three bus system having injections -6, 4, 2, at buses 1, 2, and 3, respectively. With "c"=0.5, then we will get the following distribution:
Bus 1 Bus 2 Bus 3
-6 +3 +3
-2 +4 -2
-1 -1 +2
-------------------------------------------------
-9 +6 +3 <<------
This is resulting bus distribution
from applying the "dist slack"
aij's, which does not match with the intended distribution of -6, 4, 2. Thus, you get a different set of flows.
-6 injection at bus 1
+4 injection at bus 2
+2 injection at bus 3

## Slide 26
A Complete Power Flow Calculation
For a three bus system having injections -6, 4, 2, at buses 1, 2, and 3, respectively, we need to use a single slack bus formulation (slack at bus 1) to get the following:
Bus 2 Bus 3
+4 0
0 +2
-------------------------------------------------
+4 +2
+4 injection at bus 2
+2 injection at bus 3

## Slide 27
A Complete Power Flow Calculation
Thus, in computing the "T" matrix, the "c" matrix (the one that post multiplies DAB'^-1) for our 4 bus system should appear as
          0 1 0 0
          0 0 1 0
          0 0 0 1
which means using bus # 1 as the slack in each case, that is,

## Slide 28
Additional Information
I have posted additional notes on the website, called “AdditionalSensitivityInfo.” These notes address
Efficient computation of SFs
Line outage distribution factors (LODFs)
A computationally efficient method to obtain LODFs