## Slide 1
Local Issues #1
Collection Circuits
J. McCalley

## Slide 2
Title: Transfer of Power: How President-Elect Trump’s Policies Will Affect the Energy Industry
Date: Tuesday, December 6, 2016
Time: 10:30AM - 11:30AM (Central)
Location: Room 2222 Coover
Presenters: ICF Consultants Chris MacCracken, Carol Babb, Judah Rose, Elliot Roseman, Michael Sloan, Jeff Archibald; https://www.icf.com/)
Abstract:
President-elect Trump’s positions regarding the U.S. energy sector, including his intent to “level the playing field” among generation options, appear likely to have significant impacts, including having energy play a role in job creation and economic expansion, supporting coal production and use, backing away from environmental regulation including policies related to climate change, and promoting infrastructure investment. While the stated objectives of the Trump policies tend to be straightforward, the actual impacts are likely to be influenced by the inter-relationship between different policies, of which important details are uncertain, and by political constraints. Policies favorable to natural gas and oil could negatively impact coal while environmental and power policy will influence both coal and natural gas markets. Trade policy could impact energy policy.
ICF’s views on energy markets presented during this webinar will represent an integrated perspective on energy markets that analyzes the impact of different potential policies on the overall energy market, rather than considering each policy in isolation.
In this webinar, we will discuss:
Stated positions of president-elect Trump related to the energy sector and how they are developing in the weeks following the election
Potential implications for the power, coal, and gas markets, as well as emissions regulations, should those positions become policy
How “sticky” the implications of the policies may be for decisions and investments lasting beyond the next four years
It will take time for these promises to emerge as policies and regulations, and for the interactions of those changes to be understood. To participate in the policy process under the new administration, and or to properly position business strategy, owners, developers, and investors in power and fuel supply and infrastructure must begin to consider the range of alternatives and outcomes on their strategies for the next several years.

## Slide 3
High-level design steps for a windfarm
Select site:
  Wind resource, land availability, FAA restrictions, transmission availability
Select turbine placement on site
  Wind resource, soil conditions, FAA restrictions, land agreements, constructability considerations
Select point of interconnection (POI)/collector sub
  For sites remote from nearest transmission, decide how to interconnect
    Use collector sub, collector voltage to POI (transmission sub): low investment, high losses
    Use transmission sub as collector station: high investment, low losses
  Decide via min of net present value (NPV){investment cost + cost of losses}
Design collector system
  Factors affecting design: turbine placement, POI/collector sub location, terrain, reliability, landowner requirements
  Decide via min of NPV{investment cost + cost of losses}

## Slide 4
Topologies
Usually radial feeder configuration with turbines connected in “daisy-chain” style
“’Daisy chain’ means the circuit is brought to each wind turbine,
and then the feeder continues on to the next turbine until the last
turbine is reached.” (Miller, Walling, and Piwko, “Electrical Design
of a Wind Plant,” chapter 13, in “Wind power in power systems,”
edited by T. Ackermann, second edition, 2012, Wiley.)
Usually underground cables but can be overhead
   UG is often chosen because it is out of the way from construction activities (crane travel), and of landowner activities (e.g., farming).
A feeder string may have branch strings

## Slide 5
Topologies
The five 34.5 kV feeder systems range in length from few hundred feet to several miles; have 50-100 turbines each
Source: J. Feltes, B. Fernandes, P. Keung, “Case Studies of Wind Park Modeling,” Proc. of 2011 IEEE PES General Meeting.
Note the 850MW size! There are many larger ones planned, see http://www.re-database.com/index.php/homepage/wind/the-largest-windparks
FC=“Siemens Full converter”; DFIG=“GE Double fed Ind Gen”
1119 buses, 1095 branches.

## Slide 6
More on topologies
Source: M. Altin, R. Teodorescu, B. Bak-Jensen, P. Rodriguez and P. C. Kjær, “Aspects of Wind Power Plant Collector Network Layout and Control Architecture,” available at http://vbn.aau.dk/files/19638975/Publication.
Quinonez-Varela, G.; Ault, G.W.; Anaya-Lara, O.; McDonald, J.R, “Electrical collector system options for large offshore wind farms,” Renewable Power Generation, IET, Volume: 1 , Issue: 2, 2007, pp. 107 - 114
Radially designed & radially operated
Ring designed & radially operated
Star designed & radially operated
Ring designed & radially operated
Mixed design:
Combining two of these can also be interesting, e.g., c and d.
The NO configurations may be wise under light-load conditions when the cables would otherwise produce large vars, but then they need to also be disconnected at the substation end.

## Slide 7
More on topologies
(Miller, Walling, and Piwko, “Electrical Design of a Wind Plant,” chapter 13, in “Wind power in power systems,” edited by T. Ackermann, second edition, 2012, Wiley.)
“It is conceivable that a feeder could be configured as a loop; either operated continuously in the looped configuration or with a normally open tie at the end of two radial feeders. Looping will provide increased availability, as it allows the wind turbines to operate when a feeder section is out of service. However, to operate in this mode, the feeder ampacity may have to be increased substantially from that which is required for simple radial configuration. It is common practice to taper the size of radial feeder cables and conductors as the maximum load current decreases away from the substation. If a feeder is to operate in a loop configuration, such as during an outage of a section near the substation end of one feeder, the size of cables and conductors will need to be substantially greater than for a strictly radial configuration. In addition, an extra feeder section is needed to complete the loop. The experience of the wind industry indicates that the extra investment needed to allow looped operation is not justified by the relatively small amount of recovered production otherwise made unavailable due to feeder failures. For this reason, very few wind plants employ a looped collector feeder configuration.”

## Slide 8
More on topologies
Source: S. Dutta and T. Overbye, “A clusteritering-based wind farm collector system cable layout design,” Proc of the IEEE PES. 2011 General Meeting
Radial design
Mixed design
Star design
Capital costs=cable costs+trenching costs+turbine costs+5% to account for site
preparation, grid connections, project development, and feasibility study

## Slide 9
Design considerations
Number of turbines per string is limited by conductor ampacity;
Total number of circuits limited by substation xfmr
For UG, conductor sizing begins with soil:
Soil thermal resistivity characterizes the ability of the soil to dissipate heat generated by energized & loaded power cables.
Soil resistivity is represented by Rho (ρ); units are °C-m/Watt. Lower is better: a lower value means that for a given temp differential between two points 1m apart (the numerator, similar to voltage), you get a higher heat flow or rate of change of energy (the denominator, similar to current).
ρ is the resistance to a quantity of heat flow; the thermal insulating ability of soil.
Lower value of ρ indicates better heat transfer away from cable.
ρ is the reciprocal of thermal conductivity, k [W/°C-cm].

## Slide 10
Soil thermal resistivity
Thermal resistivity depends mainly on soil composition (i.e. mineral, organics), texture (i.e. particle size grading), water content, and dry density. This complex interrelationship does not lend itself to a simple formula; testing must be carried out on any given soil to determine its resistivity.
You want high water content and high soil density (see next slide).
Air has a high thermal resistivity and therefore does not dissipate heat very well. Water dissipates heat better.
Soil with lowest thermal resistivity has maximum amount of soil grains & water.
Source: IEEE Standard 442-1981, “IEEE Guide for Soil Thermal Resistivity Measurements,” 1996.
Source: Presentation slides of Geotherm Inc., “Importance of Soil Thermal Charcteristic for Underground Power Cables., March 23, 2010, Spring 2010 ICC Meeting, Nashville, TN

## Slide 11
Soil thermal resistivity
If ρ is too high, then one can use Corrective Thermal Backfill (CTB) to significantly lower thermal resistivity.
Native soil thermal resistivities can vary from 30 to 500 °C-cm/W; corrective thermal backfill values range from 35 (wet) to 120 °C-cm/W (dry).
Source: IEEE Standard 442-1981, “IEEE Guide for Soil Thermal Resistivity Measurements,” 1996.
Source: Presentation slides of Geotherm Inc., “Importance of Soil Thermal Charcteristic for Underground Power Cables., March 23, 2010, Spring 2010 ICC Meeting, Nashville, TN

## Slide 12
Soil thermal resistivity
Adding water to a porous material decreases its thermal resistance. Units of abscissa are m3 water/m3 soil
Thermal resistivity of a dry, porous material is strongly dependent on its density. Units of abscissa are
Mega-g/m3 (106 grams/cubic meter)
Source: G. Campbell and K. Bristow, “Underground Power Cable Installations: Soil Thermal Resistivity.”
Units of ordinate in both plots are m-C/watt (so values are 0.01 of those given in cm-C/watt)

## Slide 13
Soil thermal resistivity
Source: Presentation slides of Geotherm Inc., “Importance of Soil Thermal Charcteristic for Underground Power Cables., March 23, 2010, Spring 2010 ICC Meeting, Nashville, TN

## Slide 14
Soil thermal resistivity
Source: Presentation slides of Geotherm Inc., “Importance of Soil Thermal Charcteristic for Underground Power Cables., March 23, 2010, Spring 2010 ICC Meeting, Nashville, TN

## Slide 15
Soil thermal resistivity
Source: Presentation slides of Geotherm Inc., “Importance of Soil Thermal Charcteristic for Underground Power Cables., March 23, 2010, Spring 2010 ICC Meeting, Nashville, TN
A and B correspond to conditions illustrated on previous slide
A: Wet soil (low resistivity)
B: Damp soil (high resistivity)

## Slide 16
Soil thermal resistivity
This data shows:
ρ decreases with water content
ρ decreases with amount of soil grains (e.g., compare crushed stone to uniform sand and natural sand).
ρ decreases with soil density (e.g., compare Quartz sand to Ottawa sand)
Source: IEEE Standard 442-1981, “IEEE Guide for Soil Thermal Resistivity Measurements,” 1996.

## Slide 17
Corrective thermal backfill (CTB)
CTBs and their installation can be expensive, but it does increase ampacity of a given conductor size. One therefore needs to optimize the conductor size and its corresponding cost, the associated losses, the cost of CTB, and resulting ampacity.
The below reference reports that
  “Where a total life-cycle cost evaluation is used, cable thermal ampacity tends to be a less limiting factor. This is because when lost revenue from losses are considered, optimized cable size is typically considerably larger than the size that approaches ampacity limits at peak loading.”
Source: IEEE PES Wind Plant Collector System Design Working Group, chaired by E. Camm, “Wind Power Plant Collector System Design Considerations,” IEEE PES General Meeting, 2009.
It is possible that if soil resistivity is too high, the cost of UG may be excessive, in which case overhead (or perhaps a section of overhead) can be used, if landowner allows.
Overhead incurs more outages, but UG incurs longer outage durations.
Economic consideration of losses can drive large cable size beyond thermal limitations. Note the interplay between economics, losses, and ampacity.
Double-cct trench with trefoil cables and communication conduit

## Slide 18
Fluidized thermal backfill (FTB)
Source: IEEE PES Wind Plant Collector System Design Working Group, chaired by E. Camm, “Wind Power Plant Collector System Design Considerations,” IEEE PES General Meeting, 2009.
D. Parmar, J. Steinmaniis, “Underground cable need a proper burial,”http://tdworld.com/mag/power_underground_cables_need/
CTB can be graded sand or a more highly engineered mixture referred to as fluidized thermal backfill (FTB).
FTP is a material having constituents similar to concrete but with a relatively low strength that allows for future excavation if required. FTB is generally composed of sand, small rock, cement and fly ash. FTB is installed with a mix truck and does not require any compaction to complete the installation. However, FTB is expensive, so its cost must be considered before employing it at a site.
The fluidizing component is fly-ash; its purpose is to enhance flowability and inhibit segregation of materials in freshly mixed FTB.
http://www.geothermusa.com

## Slide 19
Fluidized thermal backfill (FTB)
Source: http://www.geotherm.net/ftb.htm.
Impact of using FTB is to raise conductor ampacity.

## Slide 20
Thermal curves surrounding buried cable
Source: M. Davis, T. Maples, and B. Rosen, “Cost-Saving Approaches to Wind Farm Design: Exploring Collection-System Alternatives Can Yield Savings,” available at http://www.burnsmcd.com/BenchMark/Article/Cost-Saving-Approaches-to-Wind-Farm-Design.
Observe that the rate of temperature decrease with distance from the cable is highest in the area closest to the cables. Thus, using thermal backfill is most effective in the area surrounding the cable.

## Slide 21
Cable temperatures and backfill materials
Source: M. Davis, T. Maples, and B. Rosen, “Cost-Saving Approaches to Wind Farm Design: Exploring Collection-System Alternatives Can Yield Savings,” available at http://www.burnsmcd.com/BenchMark/Article/Cost-Saving-Approaches-to-Wind-Farm-Design.
In each case, I=500A, Ambient Temp=25 °C.
Observe cable temperature varies: 105, 81, 87 °C.
A 1000kcmil conductor was used, at 34.5kV. Soil resistivity is 1.75C-m/watt

## Slide 22
Source: M. Davis, T. Maples, and B. Rosen, “Cost-Saving Approaches to Wind Farm Design: Exploring Collection-System Alternatives Can Yield Savings,” available at http://www.burnsmcd.com/BenchMark/Article/Cost-Saving-Approaches-to-Wind-Farm-Design.
Approximate material cost of FTB is $100/cubic yard.
This three-mile segment is the “homerun” segment, which is the part that runs from the substation to the first wind turbine.

## Slide 24
The American Wire Gauge (AWG) sizes conductors, ranging from a minimum of no. 40 to a maximum of no. 4/0 (which is the same as “0000”) for solid (single wire) type conductors. The smaller the gauge number, the larger the conductor diameter.
For conductor sizes above 4/0, sizes are given in MCM (thousands of circular mil) or just cmils. MCM means the same as kcmil.
Conductor sizes
A cmil is a unit of measure for area and corresponds to the area of a circle having a diameter of 1 mil, where 1 mil=10-3 inches, or 1 kmil=1 inch.

## Slide 25
Source: M. Davis, T. Maples, and B. Rosen, “Cost-Saving Approaches to Wind Farm Design: Exploring Collection-System Alternatives Can Yield Savings,” available at http://www.burnsmcd.com/BenchMark/Article/Cost-Saving-Approaches-to-Wind-Farm-Design.
A 100 MW wind farm collection system with four feeder circuits. The amount of different kinds of conductors used in each feeder is specified.
Diameter (in)
0.398
0.522
0.813
1.0
1.118

## Slide 26
Source: M. Davis, T. Maples, and B. Rosen, “Cost-Saving Approaches to Wind Farm Design: Exploring Collection-System Alternatives Can Yield Savings,” available at http://www.burnsmcd.com/BenchMark/Article/Cost-Saving-Approaches-to-Wind-Farm-Design.
Cable cost: $1.26M
FTB cost: $265k
Total: $1.525M
Total installed cost (includes substation and labor) is $6.8M

## Slide 27
Source: M. Davis, T. Maples, and B. Rosen, “Cost-Saving Approaches to Wind Farm Design: Exploring Collection-System Alternatives Can Yield Savings,” available at http://www.burnsmcd.com/BenchMark/Article/Cost-Saving-Approaches-to-Wind-Farm-Design.
Eliminated FTB by adding an additional circuit; reduces required ampacity of homerun cable segments.
You also get increased reliability.
Cable cost: $1.255M (from $1.26M).
Total installed cost is $6.6M (from $6.8M).
Feeder circuit 5 Cable quantity (feet)
Total cable quantity (feet)
114510
49710
20100
118200
0
Four-feeder design, with FTB

## Slide 28
Source: M. Davis, T. Maples, and B. Rosen, “Cost-Saving Approaches to Wind Farm Design: Exploring Collection-System Alternatives Can Yield Savings,” available at http://www.burnsmcd.com/BenchMark/Article/Cost-Saving-Approaches-to-Wind-Farm-Design.
“For this five-feeder collection system, the overall material cost of the cable is estimated to be $1.255 million. While slightly more cable was required for the additional feeder, there was a reduction in cost due to the use of smaller cables made possible by the reduction of the running current on each of the circuits.
In this wind farm, the estimated total installed cost of the four-feeder collection
system, with FTB utilized on the homerun segments, is $6.8 million. However, when five feeders are employed, the cost decreases to $6.6 million.
Note that installing five feeders involves additional trenching, one additional circuit breaker at the collector substation, and additional protective relays and controls. But in this case, this added cost was more than offset, primarily by the absence of FTB, and to a lesser extent, the lower cost of the smaller cables.”
Design options
Observe interplay between number of cables (cost of cables, CB, relays, and controls, and trenching cost), and cost to obtain the required ampacities (circuit size and FTB).

## Slide 29
Once we specify turbine locations and # of feeders, we may make decisions via optimization
Min
Subject to:
Substation
cost
Protection cost for each feeder f
Lfs: length of feeder f, segment s
TCfs: Trench cost of feeder f, segment s
CCfsc: Conductor cost of feeder f, segment s, conductor type c
xfsc: 1 if conductor type c is chosen for feeder f, segment s, 0 if not
yfsb: 1 if backfill type b is chosen for feeder f, segment s, 0 if not
BFCfsc: backfill cost for feeder f, segment s, backfill type b
These costs given per-unit length.
A set of equations for each feeder f:
1 equation for each segment s:
Ampc is ampacity of conductor c
AFb is ampacity factor [-1,1] for backfill type b.
NTfir is number of turbines on feeder f, segment i, of rating Pr.
V is assumed line-neutral voltage of circuit, θ is assumed power factor angle
We also have equations to impose that only 1 conductor type is chosen for each segment.
The inequality causes this to be a MINLP, and so solving it will be challenging.
C is number of conductor types considered.

## Slide 30
Source: M. Davis, T. Maples, and B. Rosen, “Cost-Saving Approaches to Wind Farm Design: Exploring Collection-System Alternatives Can Yield Savings,” available at http://www.burnsmcd.com/BenchMark/Article/Cost-Saving-Approaches-to-Wind-Farm-Design.
“Due to the advantageous arrangement of the turbine and collector substation locations on this project, this outcome cannot be expected for all wind farm collection systems.
For example, collector substations are not always centrally located in the wind farm, as was the case in this particular case study. In order to reduce the length of interconnecting transmission line, they are often located off to the side of the wind farm. When this is the case, the homerun feeder segments can be several miles long. As a result, the cost of a given homerun feeder segment may exceed the cost of the remainder of the cable for that circuit. Therefore, an additional feeder design may not
always be the most economical solution.”
Design options

## Slide 31
Source: M. Davis, T. Maples, and B. Rosen, “Cost-Saving Approaches to Wind Farm Design: Exploring Collection-System Alternatives Can Yield Savings,” available at http://www.burnsmcd.com/BenchMark/Article/Cost-Saving-Approaches-to-Wind-Farm-Design.
“In those cases where a fully underground collection system may not be desirable, such as in predominantly wetland areas or in the agriculturally dense Midwest where drain tiles lead to design and construction challenges, overhead design can be considered….
The collection system homeruns and long feeder segments were considered for overhead design…. this consideration is significant because it will be carrying the feeders’ total running current. Underground homeruns can be as long as a few miles and typically require large cable sizes and an FTB envelope in order to carry these high currents….
Given that the FTB costs approximately $100 per yard, replacing underground homeruns with overhead can significantly reduce the amount, and thus cost, associated with FTB and large cable sizes used in an underground collection system….
Underground collection systems are the most preferable installations for wind farm projects. However, where underground installation may not be fully feasible, a combination of underground and overhead installation should be considered. As the case study depicts, it might make better financial sense to design an overhead collection system that is predominantly for the homerun segments.”
Design options

## Slide 32
“Either overhead lines or underground cables can be used for collector feeders. Although overhead lines are generally less expensive, a large portion of wind plants use underground cables for the following reasons:
Public acceptance of underground cables is much more favorable. This promotes positive public relations and accelerates the project permitting process. Underground cables are also more acceptable to the land owners from whom the wind plant developer must obtain rights of way.
Underground cables require less frequent maintenance and repair.
Underground cables do not impair crane access to the wind turbine tower, either during initial construction or during wind turbine repairs.
Underground cables are less disruptive to concurrent use of the land, such as for agricultural usage.
In regions with severe wind and icing, and favorable soil conditions, a direct-buried underground cable may actually be less expensive to install than an overhead line.”
Design options
(Miller, Walling, and Piwko, “Electrical Design of a Wind Plant,” chapter 13, in “Wind power in power systems,” edited by T. Ackermann, second edition, 2012, Wiley.)

## Slide 33
Source: M. Davis, T. Maples, and B. Rosen, “Cost-Saving Approaches to Wind Farm Design: Exploring Collection-System Alternatives Can Yield Savings,” available at http://www.burnsmcd.com/BenchMark/Article/Cost-Saving-Approaches-to-Wind-Farm-Design.
Design options
By replacing the underground homeruns and other long segments with overhead circuits, the total collection system cost would be reduced by approximately $1.15 million. This would result in an overall savings of approximately 17% compared to
a completely underground system.
Observe overhead saves in material costs (bare conductor vs. insulated one!) and in labor (pole installation vs. trenching).

## Slide 34
Sources: F. de Leon, “Calculation of underground cable ampacity,” CYME International T&D, 2005, available at http://www.cyme.com/company/media/whitepapers/2005%2003%20UCA-FL.pdf.
G. Anders, “Rating of Electric Power Cables: Ampacity computations for transmission, distribution, and industrial applications, IEEE Press/McGraw Hill 1997.
Cable Ampacity Calculations
One may solve the 2-dimensional diffusion equation for heat conduction:
where:
ρ: thermal resistivity of the soil
c: volumetric thermal capacity of the soil
W: rate of energy (heat) generated
The above equation can be solved using numerical methods (e.g., finite element), with boundary conditions at the soil surface. The objective is to compute the temperature at the cable for the given W (which depends on current) and ultimately, the maximum current that does not cause temperature to exceed the cable temperature rating (often 90°C). A simpler, more insightful method is the Neher-McGrath method.
Temp gradient in x direction
Temp gradient in y direction

## Slide 35
G. Anders, “Rating of Electric Power Cables: Ampacity computations for transmission, distribution, and industrial applications, IEEE Press/McGraw Hill 1997.
Neher-McGrath cable ampacity calculations
“In solving the cable heat dissipation problem, electrical engineers use a fundamental similarity between the heat flow due to the temperature difference between the conductor and its surrounding medium and the flow of electrical current caused by a difference of potential. Using their familiarity with the lumped parameter method to solve differential equations representing current flow in a material subjected to potential difference, they adopt the same method to tackle the heat conduction problem.
The method begins by dividing the physical object into a number of volumes, each of which is represented by a thermal resistance and a capacitance. The thermal resistance is defined as the material's ability to impede heat flow. Similarly, the thermal capacitance is defined as the material's ability to store heat.
The thermal circuit is then modeled by an analogous electrical circuit in which voltages are equivalent to temperatures and currents to heat flows. If the thermal characteristics do not change with temperature, the equivalent circuit is linear and the superposition principle is applicable for solving any form of heat flow problem.”

## Slide 36
Sources: F. de Leon, “Calculation of underground cable ampacity,” CYME International T&D, 2005, available at http://www.cyme.com/company/media/whitepapers/2005%2003%20UCA-FL.pdf.
G. Anders, “Rating of Electric Power Cables: Ampacity computations for transmission, distribution, and industrial applications, IEEE Press/McGraw Hill 1997.
J.H. Neher and M.H. McGrath, “The Calculation of the Temperature Rise and Load Capability of Cable Systems”, AIEE Transactions Part III - Power Apparatus and Systems, Vol. 76, October 1957, pp. 752-772.
Neher-McGrath cable ampacity calculations
Basic idea:
Subdivide the area above the conductor into layers
Model:
  heat sources as current sources
  thermal resistances as electric resistances, T
  thermal capacitance (ability to store heat) as electric capacitance – we do not need this for ss calculations
  temperature as voltage

## Slide 37
Sources: F. de Leon, “Calculation of underground cable ampacity,” CYME International T&D, 2005, available at http://www.cyme.com/company/media/whitepapers/2005%2003%20UCA-FL.pdf.
G. Anders, “Rating of Electric Power Cables: Ampacity computations for transmission, distribution, and industrial applications, IEEE Press/McGraw Hill 1997.
J.H. Neher and M.H. McGrath, “The Calculation of the Temperature Rise and Load Capability of Cable Systems”, AIEE Transactions Part III - Power Apparatus and Systems, Vol. 76, October 1957, pp. 752-772.
Neher-McGrath cable ampacity calculations
Conductor losses
Dielectric losses
of the insulation
Insul shield losses
Jacket (armor) losses
Units are w/m
Thermal resistance:
T1: conductor to insul shield
T2: insul shield to jacket
T3: jacket (or “armor”)
T4: jacket to ground surface
Units are °K-m/w)
tconductor is temp (voltage) at conductor.
texterior is temp (voltage) at exterior of cable
tambient is temp (votlage) at ground surface
GROUND SURFACE

## Slide 38
Sources: F. de Leon, “Calculation of underground cable ampacity,” CYME International T&D, 2005, available at http://www.cyme.com/company/media/whitepapers/2005%2003%20UCA-FL.pdf.
G. Anders, “Rating of Electric Power Cables: Ampacity computations for transmission, distribution, and industrial applications, IEEE Press/McGraw Hill 1997.
J.H. Neher and M.H. McGrath, “The Calculation of the Temperature Rise and Load Capability of Cable Systems”, AIEE Transactions Part III - Power Apparatus and Systems, Vol. 76, October 1957, pp. 752-772.
Neher-McGrath cable ampacity calculations

## Slide 39
Sources: F. de Leon, “Calculation of underground cable ampacity,” CYME International T&D, 2005, available at http://www.cyme.com/company/media/whitepapers/2005%2003%20UCA-FL.pdf.
G. Anders, “Rating of Electric Power Cables: Ampacity computations for transmission, distribution, and industrial applications, IEEE Press/McGraw Hill 1997.
J.H. Neher and M.H. McGrath, “The Calculation of the Temperature Rise and Load Capability of Cable Systems”, AIEE Transactions Part III - Power Apparatus and Systems, Vol. 76, October 1957, pp. 752-772.
Neher-McGrath cable ampacity calculations
Define:
Insul shield loss factor:
Armor loss factor:
Ratio of electrical losses in insul shield Ws (or electrical losses in jacket Wa) to electrical losses in conductor Wc is provided by manufacturer (equations for computing them given in Ander’s book).

## Slide 40
Sources: F. de Leon, “Calculation of underground cable ampacity,” CYME International T&D, 2005, available at http://www.cyme.com/company/media/whitepapers/2005%2003%20UCA-FL.pdf.
G. Anders, “Rating of Electric Power Cables: Ampacity computations for transmission, distribution, and industrial applications, IEEE Press/McGraw Hill 1997.
J.H. Neher and M.H. McGrath, “The Calculation of the Temperature Rise and Load Capability of Cable Systems”, AIEE Transactions Part III - Power Apparatus and Systems, Vol. 76, October 1957, pp. 752-772.
Neher-McGrath cable ampacity calculations
Substitute:
Solve for WC:
Solve for I:

## Slide 41
Sources: F. de Leon, “Calculation of underground cable ampacity,” CYME International T&D, 2005, available at http://www.cyme.com/company/media/whitepapers/2005%2003%20UCA-FL.pdf.
G. Anders, “Rating of Electric Power Cables: Ampacity computations for transmission, distribution, and industrial applications, IEEE Press/McGraw Hill 1997.
J.H. Neher and M.H. McGrath, “The Calculation of the Temperature Rise and Load Capability of Cable Systems”, AIEE Transactions Part III - Power Apparatus and Systems, Vol. 76, October 1957, pp. 752-772.
Neher-McGrath cable ampacity calculations
Given per unit length values of
Cable resistance: Rac
Cable dielectric losses: Wd
Thermal resistances: T1, T2, T3, T4
Loss factors: λ1, λ2
and given the temperature of the ground t0 and the temperature rating of the conductor tr, where Δt=tr-t0, the above equation is used to compute the rated current, Ir, or ampacity of the cable.
Identification of these parameters is described in Ch 1 of Anders book, which is available at http://media.wiley.com/product_data/excerpt/97/04716790/0471679097.pdf

## Slide 42
Sources: F. de Leon, “Calculation of underground cable ampacity,” CYME International T&D, 2005, available at http://www.cyme.com/company/media/whitepapers/2005%2003%20UCA-FL.pdf.
G. Anders, “Rating of Electric Power Cables: Ampacity computations for transmission, distribution, and industrial applications, IEEE Press/McGraw Hill 1997.
J.H. Neher and M.H. McGrath, “The Calculation of the Temperature Rise and Load Capability of Cable Systems”, AIEE Transactions Part III - Power Apparatus and Systems, Vol. 76, October 1957, pp. 752-772.
Neher-McGrath cable ampacity calculations
Usually windfarm cables, which are 3-phase, are laid out in “flat formation”, but some also use trefoil (pron tree-foil, “3 leaves” )
The previous calculation assumes the conductors are spaced so that the heating from one cable does not significantly affect the temperature seen by the conductor of the other cable. Although this calculation provides an indication of ampacity, it could be a bit lower (particularly for the one in the middle for flat formation) due to heating of the other two conductors.
Flat formation
Trefoil

## Slide 43
E. Muljadi, C. Butterfield, A. Ellis, J. Mechenbier, J. Jochheimer, R. Young, N. Miller, R. Delmerico, R. Zavadil and J. Smith, “Equivalencing the collector system of a large wind power plant,” National Renewable Energy Laboratory, paper NREL/CP-500-38930, Jan 2006. .
Equivalent collector systems
The issue: We cannot represent the collector system and all the wind turbines of a windfarm in a system model of a large-scale interconnected power grid because, assuming the grid has many such windfarms, doing so would unnecessarily increase model size beyond what is tractable. Therefore we need to obtain a reduced equivalent.
The method which follows is based on the paper referenced below; the method is now widely used for representing windfarms in power flow models.

## Slide 44
E. Muljadi, C. Butterfield, A. Ellis, J. Mechenbier, J. Jochheimer, R. Young, N. Miller, R. Delmerico, R. Zavadil and J. Smith, “Equivalencing the collector system of a large wind power plant,” National Renewable Energy Laboratory, paper NREL/CP-500-38930, Jan 2006. .
Equivalent collector systems
This is actually a large-scale windfarm, and we want to represent it as shown. Thus, we need to identify parameters Rxfmr+jXxfmr and R+jX. Our criteria is that we will observe the same losses in the equivalenced system as in the full system.

## Slide 45
E. Muljadi, C. Butterfield, A. Ellis, J. Mechenbier, J. Jochheimer, R. Young, N. Miller, R. Delmerico, R. Zavadil and J. Smith, “Equivalencing the collector system of a large wind power plant,” National Renewable Energy Laboratory, paper NREL/CP-500-38930, Jan 2006. .
Equivalent collector systems
Terminology (as used in below paper):
Trunk line: the circuits to which the turbines are directly connected.
Feeder circuits: connected to the transformer substation or the collector system substation.
All quantities in the following derivations are assumed to be in per-unit.

## Slide 46
E. Muljadi, C. Butterfield, A. Ellis, J. Mechenbier, J. Jochheimer, R. Young, N. Miller, R. Delmerico, R. Zavadil and J. Smith, “Equivalencing the collector system of a large wind power plant,” National Renewable Energy Laboratory, paper NREL/CP-500-38930, Jan 2006. .
Equivalent collector systems: trunk line level
Z1
Z2
Z3
Z4
Step 1: Derive equiv cct for daisy-chain turbines on trunk lines:
I1
I2
I3
I4
Is

## Slide 47
E. Muljadi, C. Butterfield, A. Ellis, J. Mechenbier, J. Jochheimer, R. Young, N. Miller, R. Delmerico, R. Zavadil and J. Smith, “Equivalencing the collector system of a large wind power plant,” National Renewable Energy Laboratory, paper NREL/CP-500-38930, Jan 2006. .
Z1
Z2
Z3
Z4
I1
I2
I3
I4
Is
A simplifying assumption: Current injections from all wind turbines are identical in magnitude and angle, I (a phasor).
Therefore, total current in equivalent representation is:
The voltage drop across each impedance is:
I: current phasor
n: # of turbines on trunk line.
Equivalent collector systems: trunk line level

## Slide 48
E. Muljadi, C. Butterfield, A. Ellis, J. Mechenbier, J. Jochheimer, R. Young, N. Miller, R. Delmerico, R. Zavadil and J. Smith, “Equivalencing the collector system of a large wind power plant,” National Renewable Energy Laboratory, paper NREL/CP-500-38930, Jan 2006. .
Power loss in each impedance is:
General expression for a daisy-chain trunk line with n turbines:
Total loss is given by:
Equivalent collector systems: trunk line level

## Slide 49
E. Muljadi, C. Butterfield, A. Ellis, J. Mechenbier, J. Jochheimer, R. Young, N. Miller, R. Delmerico, R. Zavadil and J. Smith, “Equivalencing the collector system of a large wind power plant,” National Renewable Energy Laboratory, paper NREL/CP-500-38930, Jan 2006. .
We just derived this:
But for our equivalent system, we get:
Equating these two expressions:
Solve for Zs:
Equivalent collector systems: trunk line level

## Slide 50
E. Muljadi, C. Butterfield, A. Ellis, J. Mechenbier, J. Jochheimer, R. Young, N. Miller, R. Delmerico, R. Zavadil and J. Smith, “Equivalencing the collector system of a large wind power plant,” National Renewable Energy Laboratory, paper NREL/CP-500-38930, Jan 2006. .
Z1
Z2
Z3
Z4
I1
I2
I3
I4
Is
Under assumption: Current injections from all wind turbines are identical in magnitude and angle, I (a phasor).
System 1:
System 2:
THEN
WHERE
Equivalent collector systems: trunk line level

## Slide 51
E. Muljadi, C. Butterfield, A. Ellis, J. Mechenbier, J. Jochheimer, R. Young, N. Miller, R. Delmerico, R. Zavadil and J. Smith, “Equivalencing the collector system of a large wind power plant,” National Renewable Energy Laboratory, paper NREL/CP-500-38930, Jan 2006. .
Step 2a: Derive equiv cct for multiple trunk lines:
Equivalent collector systems: feeder cct level
nk: number of turbines for kth trunk line
Zk: impedance for kth trunk line
Ik: current in kth trunk line = nkI
IP
By KCL:
Assume each trunk line has been equivalenced according to step 1.
System a
System b

## Slide 52
E. Muljadi, C. Butterfield, A. Ellis, J. Mechenbier, J. Jochheimer, R. Young, N. Miller, R. Delmerico, R. Zavadil and J. Smith, “Equivalencing the collector system of a large wind power plant,” National Renewable Energy Laboratory, paper NREL/CP-500-38930, Jan 2006. .
Losses:
Equivalent collector systems: feeder cct level
IP
EQUATE
System a
System b

## Slide 53
E. Muljadi, C. Butterfield, A. Ellis, J. Mechenbier, J. Jochheimer, R. Young, N. Miller, R. Delmerico, R. Zavadil and J. Smith, “Equivalencing the collector system of a large wind power plant,” National Renewable Energy Laboratory, paper NREL/CP-500-38930, Jan 2006. .
Equivalent collector systems: feeder cct level
Equating STotLoss,a to STotLoss,b, we obtain:
Solving for ZP, we get :
Generalizing the above expression:
There are N trunk lines connected to the same node, and the kth trunk line has nk turbines and equivalent impedance (based on step 1) of Zk.

## Slide 54
E. Muljadi, C. Butterfield, A. Ellis, J. Mechenbier, J. Jochheimer, R. Young, N. Miller, R. Delmerico, R. Zavadil and J. Smith, “Equivalencing the collector system of a large wind power plant,” National Renewable Energy Laboratory, paper NREL/CP-500-38930, Jan 2006. .
Under assumption: Current injections from all wind turbines are identical in magnitude and angle, I (a phasor).
System a:
System b:
THEN
WHERE
Equivalent collector systems: feeder cct level

## Slide 55
E. Muljadi, C. Butterfield, A. Ellis, J. Mechenbier, J. Jochheimer, R. Young, N. Miller, R. Delmerico, R. Zavadil and J. Smith, “Equivalencing the collector system of a large wind power plant,” National Renewable Energy Laboratory, paper NREL/CP-500-38930, Jan 2006. .
System a:
WHERE
Equivalent collector systems: compare trunk line level approach to feeder cct level approach
System b:
System 1:
System 2:
WHERE
n: Number of turbines on trunk line.
m: turbine number starting from last one
N: Number of trunk lines.
nk: number of turbines on kth trunk line

## Slide 56
E. Muljadi, C. Butterfield, A. Ellis, J. Mechenbier, J. Jochheimer, R. Young, N. Miller, R. Delmerico, R. Zavadil and J. Smith, “Equivalencing the collector system of a large wind power plant,” National Renewable Energy Laboratory, paper NREL/CP-500-38930, Jan 2006. .
Equivalent collector systems: hybrid config
What if we added impedances in our “System 1” as shown?
We would have additional losses for which we did not account for in our previous expression.
What if we added impedances in our “System a” as shown?
We would have additional losses for which we did not account for in our previous expression.

## Slide 57
E. Muljadi, C. Butterfield, A. Ellis, J. Mechenbier, J. Jochheimer, R. Young, N. Miller, R. Delmerico, R. Zavadil and J. Smith, “Equivalencing the collector system of a large wind power plant,” National Renewable Energy Laboratory, paper NREL/CP-500-38930, Jan 2006. .
These configurations are actually equivalent and are quite common. They occur when different trunk lines are connected at different points along the feeder instead of at the same feeder point.
Equivalent collector systems: hybrid config
Three trunk line equivalents,
with n1, n2, and n3 turbines, respectively.

## Slide 58
E. Muljadi, C. Butterfield, A. Ellis, J. Mechenbier, J. Jochheimer, R. Young, N. Miller, R. Delmerico, R. Zavadil and J. Smith, “Equivalencing the collector system of a large wind power plant,” National Renewable Energy Laboratory, paper NREL/CP-500-38930, Jan 2006. .
Equivalent collector systems: hybrid config
The voltage drop across each impedance is:
Losses in each impedance is:

## Slide 59
E. Muljadi, C. Butterfield, A. Ellis, J. Mechenbier, J. Jochheimer, R. Young, N. Miller, R. Delmerico, R. Zavadil and J. Smith, “Equivalencing the collector system of a large wind power plant,” National Renewable Energy Laboratory, paper NREL/CP-500-38930, Jan 2006. .
Equivalent collector systems: hybrid config
Compute losses for both systems.
IT
ZT
Equate:
Solve for ZT:

## Slide 60
E. Muljadi, C. Butterfield, A. Ellis, J. Mechenbier, J. Jochheimer, R. Young, N. Miller, R. Delmerico, R. Zavadil and J. Smith, “Equivalencing the collector system of a large wind power plant,” National Renewable Energy Laboratory, paper NREL/CP-500-38930, Jan 2006. .
Equivalent collector systems: hybrid config
Compute losses for both systems.
IT
ZT
NP: number of trunk lines
NS: number of feeder segments
(should have NP=NS)

## Slide 61
E. Muljadi, C. Butterfield, A. Ellis, J. Mechenbier, J. Jochheimer, R. Young, N. Miller, R. Delmerico, R. Zavadil and J. Smith, “Equivalencing the collector system of a large wind power plant,” National Renewable Energy Laboratory, paper NREL/CP-500-38930, Jan 2006. .
Equivalent collector systems: shunts and xfmrs
Two more issues:
Shunts: add them up (assumes voltage is 1.0 pu everywhere in collector system).
Transformers: Assume all turbine transformers are in parallel and all are the same rating. Divide transformer series impedance by number of turbines.
Bi: sum of actual shunt at bus i and line charging (Bk/2) for any circuit k connected to bus i.
Rk+jXk
Bk/2
Bk/2
Then model Btot/2 at sending-end side of feeder & at receiving-end side of feeder.
r+jx: series impedance of 1 padmount transformer.
nt: total number of transformers being equivalenced.

## Slide 62
Some final comments
All impedances should be in per-unit. The MVA base is chosen to be consistent with the power flow model for which the equivalent will be used; this is normally 100 MVA. The voltage base for a given portion of the system is the nominal line-to-line voltage of that portion of the system. Then Zbase=(VLL,base)2/S3,base.
It is sometimes useful to represent a windfarm with two or more turbines (multi-turbine equivalent) instead of just one (single-turbine equivalent), because:
  Types: A windfarm may have turbines of different types. This matters little for power flow (static) studies, but it matter for studies of dynamic performance, because in such studies, the dynamics of the machines make a difference, and the various wind turbine generators (types 1, 2, 3, and 4) have different dynamic characteristics. And so, if a windfarm has multiple types, do not form an equivalent out of different types. An exception to this may be when there are two types but most of the MW are of only one type. Then we may choose to represent all with one machine using the type comprising most of the MW.
  Wind diversity: Some turbines may see very different wind resource than other turbines. In such cases, the current output can be quite different from one turbine to another. Grouping turbines by proximity can be useful in these cases.
  Sizes (ratings): A windfarm may have different sizes, in which case the per-unit current out of the turbine for the larger sized turbines will be greater than the per-unit current out of the smaller-sized turbines. This violates the assumption that all turbines output the same current magnitude and phase. But…. there is an alternative way to address this, see next slide.

## Slide 63
Some final comments
Consider the situation where there is a daisy-chained group of turbines of different ratings, as shown below, where we observe that #1, 2 are different capacities than #3, 4.
If they are the same capacities, then the assumption they all inject identical currents holds,
and I1=I2=I3=I4=I (see slide 46-47), resulting in:
But now, I1=I2≠I3=I4. What to do?
One approach is to keep them separate, as indicated on the previous slide.

## Slide 64
Some final comments
Assume each turbine is of unique rating (most general case). Also assume that the turbines are compensated/controlled to have unity power factor Si=Pi. Then:
Assume sum of power injections=line flows:
Adding up losses and equating to loss expression of reduced model results in:

## Slide 65
Some final comments
And for pad-mounted transformers, of different sizes it can be derived (see Muljadi’s second paper)
See paper by J. Phillips for a good treatment of similar material.
Also, look into using Gaussian Elimination (see the Podmore-Germond work) to improve the collection circuit network reduction methods.