## Slide 1
Offshore Wind
J. McCalley

## Slide 2
Introduction – structures and depth
Most existing off-shore wind today is in shallow water.
M. Robinson and W. Musial, “Offshore wind technology overview,” October 2006, http://www.nrel.gov/docs/gen/fy07/40462.pdf.

## Slide 3
Introduction – structures and depth
Foundation technology for offshore wind can borrow much from designs of ocean-based oil and gas wells.
Technology White Paper on Wind Energy Potential on the U.S. Outer Continental Shelf, Minerals Management Service Renewable Energy and Alternate Use Program, U.S. Department of the Interior
May 2006, http://ocsenergy.anl.gov/documents/docs/OCS_EIS_WhitePaper_Wind.pdf.

## Slide 4
Introduction – shallow water foundations
Three types of foundations used in shallow water:
Most common
Least common

## Slide 5
Introduction – shallow water foundations
M. Robinson and W. Musial, “Offshore wind technology overview,” October 2006, http://www.nrel.gov/docs/gen/fy07/40462.pdf.

## Slide 6
Introduction – transitional depth foundations
30-90m depths
M. Robinson and W. Musial, “Offshore wind technology overview,” October 2006, http://www.nrel.gov/docs/gen/fy07/40462.pdf.

## Slide 7
Introduction – deep water foundations

## Slide 8
Introduction – deep water foundations
>60m depths
M. Robinson and W. Musial, “Offshore wind technology overview,” October 2006, http://www.nrel.gov/docs/gen/fy07/40462.pdf.

## Slide 9: Overnight cost
www.eia.gov/forecasts/aeo/assumptions/pdf/table_8.2.pdf

## Slide 10: LCOE
Offshore wind

## Slide 11: LCOE

## Slide 12
Introduction – EU growth in wind
TOTAL EU OFFSHORE WIND AT END OF 2013 IS 6562 MW
European Wind Energy Association, “The European offshore wind industry – key trends and statistics 2013,” January 2014, http://www.ewea.org/statistics/offshore/.
Cumulative MW
Annual MW

## Slide 13
Introduction - Cumulative offshore capacity
@ 2013 End
European Wind Energy Association, “The European offshore wind industry – key trends and statistics 2013,” January 2014, http://www.ewea.org/statistics/offshore/.
# of turbines, % MW
% MW
% MW
DONG – Denmark
Vattenfall – Sweden
E.ON – Germany
Centrica – UK
SSE – Ireland
RWE - Germany
BARD – Germany
Statoll –
Statkraft - UK
% MW

## Slide 14
Introduction - 2013 offshore capacity
European Wind Energy Association, “The European offshore wind industry – key trends and statistics 2013,” January 2014, http://www.ewea.org/statistics/offshore/.
# of turbines, % MW added in 2013
% MW added in 2013
MW and % MW added in 2013
DONG – Denmark
BARD – Germany
Centrica - UK
SRIW – Belgium
Colruyt – Belgium
EDF - France
E.ON – Germany
RWE – Germany
Alstom - France
% MW added in 2013

## Slide 15
Life cycle costs
Turbine cost (including tower) is 1/3 (lower than inland wind)
Support structure is 1/4 (higher than foundation for inland wind)
Grid connection is significant (higher than inland wind)
O&M is 1/4 (higher than inland wind)
 Offshore wind may scale better than inland wind
M. Robinson and W. Musial, “Offshore wind technology overview,” October 2006, http://www.nrel.gov/docs/gen/fy07/40462.pdf.

## Slide 16
Average size of turbines and wind farms
European Wind Energy Association, “The European offshore wind industry – key trends and statistics 2013,” January 2014, http://www.ewea.org/statistics/offshore/.
(added in each year)
(added in each year)

## Slide 17
US Wind Resource
US offshore wind resource at 90 m above the surface
M. Schwartz, D. Heimiller, S. Haymes, and W. Musial, “Assessment of Offshore Wind Energy Resources for the United States,” NREL/TP-500-45889, June 2010, at http://www.nrel.gov/docs/fy10osti/45889.pdf.
9m/s
3m/s

## Slide 18
US Coastal and Great Lakes Bathymetry
Bathymetry: The measurement of depth of water in oceans, seas, or lakes.
M. Schwartz, D. Heimiller, S. Haymes, and W. Musial, “Assessment of Offshore Wind Energy Resources for the United States,” NREL/TP-500-45889, June 2010, at http://www.nrel.gov/docs/fy10osti/45889.pdf.
The East coast and the Gulf of Mexico have extensive areas of shallow water relatively far from shore. On the West coast, the continental shelf descends rapidly into the deep water category. The water depth also increases rapidly away from shore around Hawaii. In the Great Lakes region, Lake Erie and portions of Lake Ontario can be characterized as shallow; the other lakes are primarily deep water, with narrow bands of shallow and transitional water near the shore.

## Slide 19
US Coastal and Great Lakes Bathymetry
NOAA National Geophysical Data Center, U.S. Coastal Relief Model, Retrieved date goes here, http://www.ngdc.noaa.gov/mgg/coastal/crm.html
From National Oceanic and Atmospheric Administration

## Slide 20
Offshore wind resource by wind speed,
water depth, distance from shore
1 n.m. = 1.15077 mi
1 n.m. = 1.852 km
These are for Georgia, but the below reference has similar data for all coastal states and great lakes.
M. Schwartz, D. Heimiller, S. Haymes, and W. Musial, “Assessment of Offshore Wind Energy Resources for the United States,” NREL/TP-500-45889, June 2010, at http://www.nrel.gov/docs/fy10osti/45889.pdf.
Arrows in table indicate influences that decrease offshore wind LCOE.

## Slide 21
Offshore wind resource by wind speed,
water depth, distance from shore
1 n.m. = 1.15077 mi
1 n.m. = 1.852 km
These are for Oregon, but the below reference has similar data for all coastal states and great lakes.
M. Schwartz, D. Heimiller, S. Haymes, and W. Musial, “Assessment of Offshore Wind Energy Resources for the United States,” NREL/TP-500-45889, June 2010, at http://www.nrel.gov/docs/fy10osti/45889.pdf.

## Slide 22
Average water depth and distance to shore of online, under construction & consented wind farms
European Wind Energy Association, “The European offshore wind industry – key trends and statistics 2013,” January 2014, http://www.ewea.org/statistics/offshore/.

## Slide 23
Horns Rev Wind Farm - Denmark
M. Robinson and W. Musial, “Offshore wind technology overview,” October 2006, http://www.nrel.gov/docs/gen/fy07/40462.pdf.
“The wind farm is located at the Danish west coast and is sited 14-20 km offshore in the North Sea, connected to shore with AC at 150 kV….a single 150 kV sub sea-power cable is in operation. Since the turbines are connected with 34 kV, an additional platform with the 34 to 150 kV transformer was necessary.”
J. Schachner, “Power connections for offshore wind farms,” MS thesis, TUDelft, 2004.
34 to 150 kV transformer
North Sea!

## Slide 24
North Sea Offshore, Existing & Under construction, 7/2011
K. Veum, L. Cameron, D. Hernando, M. Korpas, “Roadmap to the deployment of offshore wind energy in the central & southern North Sea: 2020-2030,” July 2011, at www.windspeed.eu/media/publications/WINDSPEED_Roadmap_110719_final.pdf.
EXISTING
Under cnstrctn
Of 2913 MW EU offshore, 1866 MW is in North Sea

## Slide 25
North Sea Offshore Potential
K. Veum, L. Cameron, D. Hernando, M. Korpas, “Roadmap to the deployment of offshore wind energy in the central & southern North Sea: 2020-2030,” July 2011, at www.windspeed.eu/media/publications/WINDSPEED_Roadmap_110719_final.pdf.

## Slide 26
North Sea Offshore Potential
K. Veum, L. Cameron, D. Hernando, M. Korpas, “Roadmap to the deployment of offshore wind energy in the central & southern North Sea: 2020-2030,” July 2011, at www.windspeed.eu/media/publications/WINDSPEED_Roadmap_110719_final.pdf.
(little shallow or deep water
(mainly shallow water)
(mainly deep water)
(both shallow and deep water)

## Slide 27
Interactions between sea use functions
K. Veum, L. Cameron, D. Hernando, M. Korpas, “Roadmap to the deployment of offshore wind energy in the central & southern North Sea: 2020-2030,” July 2011, at www.windspeed.eu/media/publications/WINDSPEED_Roadmap_110719_final.pdf.

## Slide 28
Typical offshore layout
M. Robinson and W. Musial, “Offshore wind technology overview,” October 2006, http://www.nrel.gov/docs/gen/fy07/40462.pdf.
J. Schachner, “Power connections for offshore wind farms,” MS thesis, TUDelft, 2004.
An excellent tutorial on cable-laying is given here:
http://www.iscpc.org/publications/About_SubPower_Cables_2011.pdf and is stored in my resource file.

## Slide 29
DC-thyristor vs DC-VSC
S. Meier, S. Norrga, H.-P. Nee, ‘’New voltage source converter topology for HVDC grid connection of offshore wind farms,’’ at http://www.ee.kth.se/php/modules/publications/reports/2004/IR-EE-EME_2004_013.pdf.
HVDC transmission uses either thyristor-based converters or voltage source converters (VSC). Most DC designs for offshore wind utilize VSC because VSC is more economic at these lower power ratings.

## Slide 30
AC vs DC-thyristor vs DC-VSC
M. Bahrman, HVDC Transmission Overview, .
AC
AC
DC
DC
Line commutated current source converter.
Self-commutated voltage source converter
Notes: Voltage source inverters use the dc voltage (e.g a capacitor in parallel) as a source while the current source inverter (inductor in series) use the dc current as a source (voltage can not be changed abruptly in capacitor and current can not be changed abruptly in inductor)

## Slide 31
An interesting idea
VSC
PMG
VSC
Wind farm
AC
VSC
VSC
On-shore power grid
DC
AC
DC
AC
Wind turbine
Sea-bed transmission
VSC
PMG
Wind farm
AC
VSC
On-shore power grid
DC
AC
Wind turbine
Sea-bed transmission

## Slide 32
AC vs DC-thyristor vs DC-VSC
AC requires no converter station but has high charging (capacitive) currents that become excessive for long distances. An important issue with AC is whether to step up to transmission voltage in the sea and then transport over high voltage or transport over lower (34.5 kV) voltage and step up to transmission inland.
DC-thyristor has very high power handling capability but converter stations are expensive, and they have short-circuit limitations and therefore locational constraints.
DC-VSC (voltage-source converters) have lower power-handling capabilities, but converter stations are less expensive and they have no short-circuit limitations and can therefore be located anywhere.
J. Schachner, “Power connections for offshore wind farms,” MS thesis, TUDelft, 2004.

## Slide 33
AC vs DC-thyristor vs DC-VSC
J. Schachner, “Power connections for offshore wind farms,” MS thesis, TUDelft, 2004.
Switchgear & converters

## Slide 34
Losses vs. distance for different AC voltage
J. Schachner, “Power connections for offshore wind farms,” MS thesis, TUDelft, 2004.
Power losses for HV (132 kV) and MV (34 kV)
Compare 132 kV to 34 kV for 250MW transmission
Compare 132 kV to 34 kV for 100MW transmission
Compare 132 kV to 34 kV for 50MW transmission

## Slide 35
Breakover distances for AC vs DC
J. Schachner, “Power connections for offshore wind farms,” MS thesis, TUDelft, 2004.
I believe this is for net present worth of {investment + operating costs} but source does not say. But displayed concepts are right:
AC w/farm voltage transmission is only right for short distances at low power
AC w/offshore transformation is right for medium distances at medium power
DC is right for long distances or at high power transfer.

## Slide 36
STANDARD NETWORK TOPOLOGIES
J. Schachner, “Power connections for offshore wind farms,” MS thesis, TUDelft, 2004.
This is similar to inland topologies, but here, the location of the step-up transformer is more influential in the economics of the design.
RADIAL
(STRING)
STAR
FARM-VOLTAGE TRANSMISSION
OFF-SHORE TRANSFORMATION

## Slide 37
Costs, Reliability & Losses
J. Schachner, “Power connections for offshore wind farms,” MS thesis, TUDelft, 2004.
“For large scale OWFs a combination of these basic layouts is commonly used, where several strings of turbines are connected to the shore connection point. Its advantages are the simpler cable laying pattern and the shorter cable lengths compared to a strictly star layout. The disadvantages occur with cable failure, because all the turbines upward the failure site on a string have to be switched off and cannot be connected to the grid until the failure has been repaired. Especially during periods of harsh sea conditions in winter the required repair time can be months. Also the number of turbines which can be connected to a string is limited by the power carrying capability of the cable used. With growing turbine power output, the star connection offers the possibility to reduce cable losses by clustering small groups of turbines to high voltage transformer stations as shown in layout IV. Also in case of cable failure at a turbine connection only the single turbine where the failure occurred has to be switched off, the remaining turbines connected to the transformer platform can stay in operation. The big disadvantage is the required transformer platform.”
Off-shore windfarms

## Slide 38
Wake Interactions
K. Veum, L. Cameron, D. Hernando, M. Korpas, “Roadmap to the deployment of offshore wind energy in the central & southern North Sea: 2020-2030,” July 2011, at www.windspeed.eu/media/publications/WINDSPEED_Roadmap_110719_final.pdf.
Wakes behind wind turbines at Horns Rev

## Slide 39
Off-shore wind farm siting
K. Veum, L. Cameron, D. Hernando, M. Korpas, “Roadmap to the deployment of offshore wind energy in the central & southern North Sea: 2020-2030,” July 2011, at www.windspeed.eu/media/publications/WINDSPEED_Roadmap_110719_final.pdf.
“In view of the recent findings on wakes within offshore wind farms and on wind speed deficits behind these wind farms, the WINDSPEED project considers that, within a defined area, only 30% of the total should realistically be occupied by wind farms. It is assumed that any large scale deployment of offshore wind will likely take the form of multiple wind farm clusters uniformly spaced, allowing adequate distance between each cluster to mitigate the impact of inter wind farm wake losses and the resulting lost production and wake turbulence loading …The remaining 70% shall provide space for wind speed recovery and dissipation of wake turbulent energy, but also possibly permit some form of navigation throughout the area …This provides opportunities for co-use/co-existence with other sea uses such as shipping and fishing.”
“D” is turbine diameter.

## Slide 40
North Sea HVDC Network?
K. Veum, L. Cameron, D. Hernando, M. Korpas, “Roadmap to the deployment of offshore wind energy in the central & southern North Sea: 2020-2030,” July 2011, at www.windspeed.eu/media/publications/WINDSPEED_Roadmap_110719_final.pdf.
“For those scenarios in which some form of offshore grid is assumed to develop – the In the Deep and Grand Design scenarios – the results from the DSS were used to define a number of potential OWE clusters along with onshore connection points. An offshore grid was then designed that interconnects these wind clusters and onshore connection points in such a way as to optimise the investment cost of the grid against the benefit it provides by increased trade opportunities and connections to the new offshore wind generation units.”
Decision-support system
D. Huertas Hernando, M. Korpas, S. vsn Dyken, “Grid Implications: Optimal design of a subsea power grid in the North Sea,” WP6 Final Report D6.3, June 2011.

## Slide 41
Wind-motivated networks?
Is there a “multi-farm collection network” problem that is general/common to both inland & offshore?
There would be differences in implementation, but design method may be very similar.

## Slide 42
sd
sd
2010 SmartTransmission Study
2008 Joint Coordinated System Plan
2013 Rock Island Clean Line
2010 Green Power Express
2011 MISO RGOS Study
High Capacity Transmission for Iowa

## Slide 43
GIS-based wind farm site potential
PINK: Sufficient wind speed; feasible area
BLUE: Sufficient wind speed; infeasible area
BLACK: Insufficient wind speed; feasible area
RED: Insufficient wind speed; infeasible area
Feasibility: land cvr, cities/towns, protected, FAA, exstng WF
Feasible sites > 21 mi2; Sufficient wind>7m/s at 80m
Each square is 5x5 miles; 8MW/mi2 (200MW/square)
927 squares are PINK (sufficient wind and feasible site)

## Slide 44
Iowa Transmission System with New Backbone
Derived from public data:
  IUB map, FERC filings, utility websites, EIA, MTEP
Existing system model includes:
transmission >100kV
  319 transmission lines,
  204 nodes, 99 loads,
  81 generators, 40 wind farms
5 bordering states:
gen/load represented at single node
Backbone design:
utilized MTEP-2011 plans + 765kV
loop to connect wind intense areas
with load centers in Iowa & eastward.
THICK PURPLE: 765 kV backbone
THICK RED: New 345kV

## Slide 45
Wind Farm Site Identification
10 GW Future
30 GW Future
20 GW Future
765kV Overlay | 10GW | 20GW | 30GW
New Capacity (MW) | 4954 | 14956 | 24960
New Wind Farms (1 windfarm = 200MW square) | 27 | 79 | 133
CF of New Wind | 0.3824 | 0.3751 | 0.3708
Mean Distance (mi) | 4.33 | 6.52 | 8.68
Select sites to satisfy target GW level while minimizing {cost of turbines + cost of transmission} per MWhr.

## Slide 46
R2B Transmission Design Results
A
B
C
D
E
F
G
H
Transmission designs for each cluster minimize investment costs while satisfying N-1 reliability constraints (20 GW future).

## Slide 47
R2B Transmission Design Results
A
B
C
D
E
F
G
H
765kV Overlay 20GW Scenario |  |  |  |  |  |  |  |  |  |  |  |  |  | 
 | Wind Farms | Paths | Ccts | 161 Sngle | 161 High | 345 Sngle | 161 Dble | 345 Dble | ROW Miles | Circuit Miles | Cost $M |  | cct miles / Wind Farm | $M/ct/mi
A | 15 | 19 | 24 | 10 | 4 | 0 | 3 | 2 | 109.1 | 133.6 | 120.3 |  | 8.91 | 0.90
B | 11 | 13 | 20 | 6 | 0 | 0 | 6 | 1 | 61.4 | 92.9 | 75 |  | 8.45 | 0.81
C | 13 | 18 | 25 | 10 | 1 | 0 | 6 | 1 | 93.5 | 127.3 | 101.7 |  | 9.79 | 0.80
D | 9 | 12 | 15 | 9 | 0 | 0 | 2 | 1 | 66.2 | 80.2 | 68 |  | 8.91 | 0.85
E | 11 | 17 | 17 | 17 | 0 | 0 | 0 | 0 | 120.3 | 120.3 | 96.2 |  | 10.94 | 0.80
F | 5 | 6 | 9 | 3 | 0 | 0 | 3 | 0 | 48 | 77.2 | 58.8 |  | 15.44 | 0.76
G | 6 | 8 | 10 | 4 | 2 | 0 | 1 | 1 | 49.3 | 62.4 | 59.1 |  | 10.40 | 0.95
H | 6 | 7 | 11 | 3 | 0 | 0 | 4 | 0 | 42.9 | 64.8 | 49.7 |  | 10.80 | 0.77
All | 76 | 100 | 131 | 62 | 7 | 0 | 25 | 6 | 590.7 | 758.7 | 628.8 |  | 9.98 | 0.83

## Slide 48
Wind-motivated networks?
Some thinking on novel designs:
T. Hammons, V. Lescale, K. Uecker, M. Haeusler, D. Retzmann, K. Staschus, S. Lepy, “State of the Art in Ultrahigh-Voltage Transmission,” Proceedings of the IEEE, Vol. 100, No. 2, February 2012.

## Slide 49
Wind-motivated networks?
See 2012 class paper by Khondkar Hasan for an intersting hybrid offshore wind-hydrokinetic wind system design, with associated summarization of other hydrokinentic designs.