Module PE.PAS.U19.5

Generation adequacy evaluation

# U19.1	Introduction

Probabilistic evaluation of generation adequacy is traditionally performed for one of two classes of decision problems. The first one is the generation capacity planning problem where one wants to determine the long-range generation needs of the system. The second one is the short-term operational problem where one wants to determine the unit commitment over the next few days or weeks.

We may think of the problem of generation adequacy evaluation in terms of Fig. U19.1.

Fig. U19.1: Evaluation of Generation Adequacy

In Fig. U19.1, we see that there are a number of generation units, and there is a single lumped load. Significantly, we also observe that all generation units are modeled as if there were connected directly to the load, i.e., transmission is not modeled. The implication of this is that, in generation adequacy evaluation, transmission is assumed to be perfectly reliable.

We begin our treatment by first identifying the necessary modeling requirements in terms of, in Section U19.2, the generation side, and, in Section U19.3, the load side. Section U19.4 describes a common computational approach associated with the generation capacity planning problem, and Section U19.5 illustrates how this approach is typically used for capacity planning. Section U19.6 provides an alternative way of computing generation capacity planning indices. Section U19.7 briefly summarizes three important issues central to a more extended treatment of the topic.

# U19.2	Generator model

In the basic capacity planning study, each individual generation unit is represented using the two-state model illustrated in Fig. U19.2.

Fig. U19.2: Two-State Model

This model was described in Sections U16.4-U16.5 and Section U18.2.3 of modules U16 & U18, respectively. Important relations for this model, in terms of long-run availability A and long-run unavailability U, are provided here again, for convenience.

(U19.1)

(U19.2)

Module U18 also describes how one can approximate the effects of derating and, for peaking plants, of reserve shutdown, by using equivalent forced outage rate, EFOR, according to:

(U19.3)

Module 18 also describes a four state model to capture the effects of being in reserve shutdown.

## U19.2.1 Capacity outage table for identical units

A capacity table is simply a probabilistic description of the possible capacity states of the system being evaluated. The simplest case is that of the 1 unit system, where there are two possible capacity states: 0 and C, where C is the maximum capacity of the unit. Table U19.1 shows capacities and corresponding probabilities.

Table U19.1: Capacity Table for 1 Unit System

| Capacity | Probability |
| --- | --- |
| C | A |
| 0 | U |

We may also describe this system in terms of capacity outage states. Such a description is generally given via a capacity outage table, as in Table U19.2.

Table U19.2: Capacity Outage Table for 1 Unit System

| Capacity Outage | Probability |
| --- | --- |
| 0 | A |
| C | U |

Figure U19.3 provides the probability mass function (pmf) for this 1 unit system.

Fig. U19.3: pmf for Capacity Outage of 1 Unit Example

Now consider a two unit system, with both units of capacity C. We can obtain the capacity outage table by basic reasoning, resulting in Table U19.3.

Table U19.3: Capacity Outage Table for 2 Identical Units

| Capacity Outage | Probability |
| --- | --- |
| 0 | A2 |
| C | AU |
| C | UA |
| 2C | U2 |

We may also more formally obtain Table U19.3 by considering the fact that it provides the pmf of the sum of two random variables. Define X1 as the capacity outage random variable (RV) for unit 1 and X2 as the capacity outage RV for unit 2, with pmfs fX1(x) and fX2(x), each of which appear as in Fig. U19.3. We desire fY(y), the pmf of Y, where Y=X1+X2. Recall from Section U13.3.2 that we can obtain fY(y) by convolving fX1(x) with fX2(x), i.e.,

(U19.4)

But, inspection of fX1(x) and fX2(x), as given by Fig. U19.3, indicates that, since X1 and X2 are discrete random variables, their pmfs are comprised of impulses. Convolution of any function with an impulse function simply shifts and scales that function. The shift moves the origin of the original function to the location of the impulse, and the scale is by the value of the impulse. Fig. U19.4 illustrates this idea for the case at hand.

Fig. U19.4: Convolution of Generator Outage Capacity pmfs

Figure U19.5 shows the resultant pmf for the capacity outage for 2 identical units each of capacity C.

Fig. U19.5: pmf for Capacity Outage of 2 Unit Example

We note that Fig. U19.5 indicates there are only 3 states, but in Table U19.3, there are 4. One may reason from Table U19.3 that there are two possible ways of seeing a capacity outage of C, either unit 1 goes down or unit 2 goes down. Since these two states are the same, we may combine their probabilities, resulting in Table U19.4, which conforms to Fig. U19.5.

Table U19.4: Capacity Outage Table for 2 Identical Units

| Capacity Outage | Probability |
| --- | --- |
| 0 | A2 |
| C | 2AU |
| 2C | U2 |

In fact, we saw this same kind of problem in Section U10.2 of module 10, where we showed that the probabilities can be handled using a binomial distribution, since each unit may be considered as a “trial” with only two possible outcomes (up or down). We may then write the probability of having r units out of service as:

(U19.5)

It is of interest to note that we may also think about this problem via a state-space model, as shown in U19.6 where we have indicated the state of each unit together with the capacity outage level associated with each system state. Note that we are not representing the possibility of common mode or dependent failures.

Fig. U19.6: State Space Model for 2-Unit System

From Section U16.8 of module 16, since the two middle states of Fig. U19.3 satisfy the merging condition (a group of (internal) states can be merged if the transition intensities to any external states are the same from each internal state.) and they satisfy rule 3 (two states should be combined only if they are of the same state classification – in this case, the same capacity), we may combine them using rule 1 (when two (internal) states have transition rates that are identical to common external states, those two states can be merged into one; entry rates are added, exit rates remain the same.) Therefore, Fig. U19.6 becomes Fig. U19.7.

Fig. U19.7: Reduced State Space Model for 2 Unit System

The 2λ transition in Fig. U19.6 reflects the fact that the “0 out” state may transition to the “C out” state because of unit 1 or because of unit 2, but it does not reflect a common mode outage since the middle state is a state in which only 1 unit is failed. Similarly, the 2( transition in Fig. U19.6 reflects the fact the “2C out” state may transition to the “C out” state because of repair to unit 1 or repair to unit 2, but it does not reflect a common mode repair since the middle state is a state in which only 1 unit is repaired.

One may also compute frequency and duration for each state in Fig. U19.7 according to (U16.32) and (U16.33), repeated here for convenience:

(U19.6)

(U19.7)

Table U19.5 tabulates all of the information.

Table U19.5: Capacity Outage Table for 2 Identical Units with Frequencies and Durations

| Capacity Outage | Probability | Frequency | Duration |
| --- | --- | --- | --- |
| 0 | A2 | 2λA2 | 1/2λ |
| C | 2AU | 2AU(λ | 1/(λ |
| 2C | U2 | 2(U2 | 1/2( |

U19.2.2 Capacity outage table for units having different capacities

Reference [1] provides a simple example for the more realistic case of having multiple units with different capacities, which we adapt and present here. Consider a system with two 3 MW units and one 5 MW unit, all of which have forced outage rates (FOR) of 0.02. (The fact that all units have the same FOR means that we could handle this using the binomial distribution, which would not be applicable if any unit had a different FOR).

The pmfs of the two identical 3 MW units can be convolved as in Section U19.2.1 to give the pmf of Fig. U19.8 and the corresponding capacity outage table of Table U19.6.

Fig. U19.8: pmf for Capacity Outage of Convolved 3 MW Units

Table U19.6: Capacity Outage Table for Convolved 3 MW Units

| Capacity Outage | Probability |
| --- | --- |
| 0 | 0.982=0.9604 |
| 3 | 2(0.98)(0.02)=0.0392 |
| 6 | 0.022=0.0004 |

Now we want to convolve in the 5 MW unit. The pmf for this unit is given by Fig. U19.9.

Fig. U19.9: pmf for 5 MW Capacity Outage

Convolving the pmf of Fig. U19.8 with the pmf of Fig. U19.9 results in the pmf illustrated in Fig. U19.10, with the corresponding capacity outage table given in Table U19.7.

Table U19.7: Capacity Outage Table for Convolved 3 MW Units and 5 MW Unit

| Capacity Outage | Probability |
| --- | --- |
| 0 | 0.9604(0.98=0.941192 |
| 3 | 0.98(0.0392=0.038416 |
| 5 | 0.02(0.9604=0.019208 |
| 6 | 0.98(0.0004=0.000392 |
| 8 | 0.02(0.0392=0.000784 |
| 11 | 0.02(0.0004=0.000008 |

Fig. U19.10: Procedure for convolving Two 3 MW units with 5 MW Unit (top two plots) and final 3 unit pmf

## U19.2.3	Convolution algorithm

The procedure illustrated above can be expressed algorithmically, which is advantageous in order to code it.

Two-state model:

The algorithm is simplest if we assume that all units are represented using two-state models.

Let k denote the kth unit to be convolved in, Ak and Uk its availability and FOR, respectively, and Ck its capacity.

The composite capacity outage pmf before a convolution is denoted by fYold(y), and after by fYnew(y), so that for unit k, the capacity outage random variables are related by Ynew=Yold+Xk. We assume that there are N units to be convolved.

The algorithm follows.

- Let k=1.

- Convolve in the next unit according to:

(U19.8)

for all values of y for which fYold(y)(0  and fYold(y-Ck) (0.

- If k=N, stop, else go to 2.

Note that in (U19.8) the influence of the argument in the last term fYold(y-Ck) is to shift the function fYold(y) to the right by an amount equal to Ck. This corresponds to the shift influence of the kth unit pmf impulse at Xk=Ck.

## U19.2.4 Deconvolution

An interesting situation frequently occurs, particularly in operations, but also in production costing programs, when the composite pmf has been computed for a large number of units, and capacity outage probabilities are fully available. Then one of the units is decommitted, and the existing composite pmf no longer applies. How to obtain a new one?

One obvious approach is to simply start over and perform the convolution for each and every unit. But this is time-consuming, and besides, there is a much better way! We have a better approach based on the following fact:

The computation of fYnew(y) is independent of the order in which the units are convolved.

Consider, in (U19.8), the term fYold(y). This is the composite pmf just before the “last” unit was convolved in.

Given we have fYnew(y), we assume that the “last” unit convolved in was the unit that we would like to decommit.

It may not have been the last unit, in actuality, but because the computation of fYnew(y) is independent of order, we can make this assumption without loss of generality.

In that case, we may “convolve out” the decommited unit.

How to do that? Consider solving (U19.8) for fYold(y), resulting in:

(U19.9)

The problem with the above is that the function we want to compute on the left-hand-side, fYold(y), is also on the right-hand-side, as fYold(y-Ck).

There is a way out of this, however. It stems from two facts.

Fact 1: The probability of having capacity outage less than 0 is zero, i.e., the “best” that we can do is that we have no capacity outage, in which case the capacity outage is zero. Therefore any valid capacity outage pmf must be zero to the left of the origin.

Fact 2: fYold(y-Ck) is a valid capacity outage pmf.

Implication: For values of y such that 0<y<Ck, fYold(y-Ck) evaluates to the left of the origin and therefore, since fYold is a valid capacity outage pmf, it MUST BE ZERO in this range. As a result,

(U19.10)

But what about the case of Ck<y<IC, where IC is the total installed capacity? Here, we must use (U19.9). But let’s assume that we have already computed fYold(y) for 0<y<Ck. Then the first time we use (U19.9) is when y=Ck. Then we have:

But we already have computed fYold(0) from (U19.10)!

And we will be able to use the values of fYold(y), 0<y<Ck, in computing all values of fYold(y), Ck<y<2Ck. In fact, we will be able to compute all of the remaining values of fYold(y) in this way!

As an example, try deconvolving one of the 3 MW units from the capacity outage table of Table U19.7 (which is also illustrated at the bottom of Fig. U19.10). In this case, C3=3, A3=0.98, U3=0.02. The computations are given in Table U19.8. The last calculation in Table U19.8 is negative. This is due to roundoff error, which can become significant for very small probabilities. This particular value, for y=11, should be zero.

Note that, since fYold(y-Ck)=0 for y<Ck, (U19.9) includes the case of (U19.10), and we can express the algorithm using (U19.9) only. The deconvolution algorithm is given below. There is just one step. We assume that we are deconvolving unit k.

- Compute:

consecutively for y=0, ….,IC such that

fYnew(y)(0,  fYold(y-Ck)(0,

where IC is the installed capacity of the system before deconvolution.

- Stop.

Table U19.8: Computations for Deconvolution Example

| Capacity Outage y | fYnew(y) | fYold(y) |
| --- | --- | --- |
| 0 | 0.94119200 |  |
| 3 | 0.0384160 |  |
| 5 | 0.019208 |  |
| 6 | 0.00039200 |  |
| 8 | 0.00078400 |  |
| 11 | 0.00000800 |  |

## U19.2.5 Multi-state models

We have so far addressed only the case where all units are represented by two-state models. It may be, however, that we would like to account for derated units, in which case we need to address the multi-state model as well. This situation presents no additional conceptual difficulty relative to the two-state model, as the pmf for each unit will still consist of only impulses, except now, each unit will have a pmf consisting of as many impulses as it has states, instead of only two.

We do, however, need to generalize the algorithms for convolution and deconvolution.

Convolution algorithm for multi-state case:

With N the total number of units:

- Let k=1.

- Convolve in the next unit according to:

(U19.11)

for all values of y for which fYold(y) or fYold(y-Ckj) are non-zero. Here, nk is the number of states for unit k; pkj is the jth state probability for unit k; Ckj is the jth capacity outage for unit k.

- If k=N, stop, else go to 2.

Note that (U19.11) is the same as (U19.8) if nk=2, with Ak=pk1, and Uk=pk2.

Deconvolution algorithm for multi-state case:

We again assume that we are deconvolving unit k. To determine the deconvolution equation for the multi-state case, rewrite (U19.11) by extracting from the summation the first term, according to:

where we have assumed that the first capacity outage state for unit k is zero, i.e., Ck1=0. Solving for fYold(y), we have:

We assume that we are deconvolving unit k. The algorithm is:

- Compute:

(U19.12)

consecutively for y=0, ….,IC, and y such that fYnew(y)(0,  fYold(y-Ckj)(0, where IC is the installed capacity of the system before deconvolution.

- Stop.

# U19.3	Load model

Consider the plot of instantaneous demand as a function of time, as given in Fig. U19.11.

Fig. U19.11: Instantaneous load vs. time

Although this curve is only illustrated for seven days, one could easily imagine extending the curve to cover a full year.

From such a yearly curve, we may identify the percent of time for which the demand exceeds a given value. If we assume that the curve is a forecasted curve for the next year, then this percentage is equivalent to the probability that the demand will exceed the given value in that year.

The procedure for obtaining the percent of time for which the demand exceeds a given value is as follows.

- Discretize the curve into N equal time segments, so that the value of the discretized curve in each segment takes on the maximum value of continuous curve in that segment.

- The percentage of time the demand exceeds a value d is obtained by counting the number of segments having a value greater than d and dividing by N.

- Plot the demand d against the percent of time the demand exceeds a value d. A typical such plot is illustrated in Fig. U19.12.

Fig. U19.12: Load duration curve

Fig. U19.12 is often generically referred to as a load duration curve (LDC). However, one should be aware that there is a significant difference between LDCs based on hourly segments and LDCs based on daily segments.

- Hourly: the load duration curve indicates the percentage of hours through the year that the hourly peak exceeds a value d.

- Daily: the load duration curve indicates the percentage of days through the year that the daily peak exceeds a value d.

Thus, one must realize that the load duration curve gives the percentage of time through the year that the load exceeds a value d, only under the assumption that

- Hourly: the load is constant throughout the hour at the hourly peak.

- Daily: the load is constant throughout the day at the daily peak.

Clearly, the smaller the segment, the better approximation is given by the LDC to the actual percentage of time through the year that the load exceeds a value d. Nonetheless, both daily and hourly-based LDCs are used in practice.

The LDC may also be drawn in another way that is convenient for computation. Consider first normalizing the abscissa (x-coordinate) by dividing all values by 100, so that we obtain all abscissa values in the range of 0 to 1.

The abscissa then represents the probability that the demand exceeds the corresponding value d. We denote this probability using the notation for a cumulative distribution function (cdf), FD(d). However, one should realize that it is actually the complement of a true cdf, i.e.,

Here, D is a random variable and d are the values it may take.

Finally, we can switch the axes of the LDC so that we plot FD(d) as a function of d. Figure U19.12 illustrates the curve, which we refer to as the load shape for the given time period.

Fig. U19.12: Load shape

Note that Chanan Singh in his notes on “Load Modeling” gives an algorithm for getting the load model from a single scan of the hourly load data [12].

# U19.4	Calculation by Capacity Outage Tables

Module U17 identifies the loss of load probability (LOLP) and the loss of load expectation (LOLE) as two indices for characterizing generation adequacy risk. The LOLP is the probability of losing load throughout the time interval (year). LOLE is the number of time units (hours or days) per time interval (year) for which the load will exceed the demand.

Fig. U19.13 illustrates a typical load-capacity relationship [1] where the load model is shown as a continuous curve for a period of 365 days. The capacity outage state, Ck, is shown so that one observes that load interruption only occurs under the condition that d>IC-Ck. The minimum demand for which this is the case is dk=IC-Ck. Thus, the probability of having an outage of capacity Ck and of having the demand exceed dk is given by the capacity outage pmf and FD(dk), i.e., fY(Ck)FD(dk)= fY(Ck)FD(IC-Ck).

Fig. U19.13: Relationship between capacity outage, load model [1]

The LOLP is then computed as:

(U19.13)

and the LOLE as:

(U19.14)

where N is the total number of capacity outage states.

Example: Compute the LOLP and the LOLE for the capacity outage table of Table U19.7, for the load shape curve given by Fig. U19.14. Table U19.7 is repeated below for convenience.

Table U19.7: Capacity Outage Table for Convolved 3 MW Units and 5 MW Unit

| Capacity Outage | Probability |
| --- | --- |
| 0 | 0.9604(0.98=0.941192 |
| 3 | 0.98(0.0392=0.038416 |
| 5 | 0.02(0.9604=0.019208 |
| 6 | 0.98(0.0004=0.000392 |
| 8 | 0.02(0.0392=0.000784 |
| 11 | 0.02(0.0004=0.000008 |

Fig. U19.14: Load shape curve for example

From (U19.13), we then have:

We could compute LOLE using (U19.14), but it is easier to just recognize that

LOLE=LOLP*365=0.008044*365 =2.93606 days/year.

This means that we can expect to see 2.93606 complete days of load interruption each year, assuming that the peak load per day lasts all day. Another index often cited is the years/day, in this case, 1/2.93606=0.3406 years/day. This is the number of years that must pass before we see a full day of load interruption.

Two important qualifiers should be emphasized:

- This is the load outage time expected as a result of generation unavailability and does not include the effects of transmission or distribution system components unavailability.

- This amount of outage time would correspond to the long-run average of this system only if

  - all 3 units are always committed, i.e., no reserve shutdown, and there is no maintenance

  - the demand remains at its peak throughout the day

These qualifiers are obviously pointing towards inaccuracies in the model and as a result, indicate that the indices computed should not be perceived as accurate in an absolute sense. However, the indices should still serve well for comparative purposes.

# U19.5	A capacity planning example

Reference [1] provides an illustrative example showing how the generation adequacy calculation procedure in the previous section can be applied to the capacity planning problem. We adapt that example here.

Consider a system containing five 40 MW units each with a FOR=0.01, so that the installed capacity is 200 MW.

The capacity outage table for this system is shown in Table U19.9, where capacity outage states having probabilities less than 10-6 have been neglected.

Table U19.9: Capacity outage table for example [1]

| Capacity Outage | Probability |
| --- | --- |
| 0 | 0.950991 |
| 40 | 0.048029 |
| 80 | 0.000971 |
| 120 | 0.000009 |

The next years’s system load model is represented by the load shape curve of Fig. U19.15, which is a linear approximation of an actual load shape curve. Note that the forecasted annual system peak load is 120 MW.

Fig U19.15: Load shape curve for example [1]

The procedure of the previous section was applied and the LOLE and years/day were computed as 0.002005 days/year and 498 years/day, respectively. Certainly this is a very reliable system! The reason for the high reliability is, of course, that the installed capacity is so much greater than the system annual peak.

However, the load will grow in the future, so it is of interest to see how these indices vary as peak load increases. Table U19.10 summarizes LOLE and years/day for the system peak beginning at 120 MW and increasing to 200 MW in units of 10 (this is to just illustrate the effect on the indices; the 10 MW increment should not be interpreted as an annual load growth).

Table U19.10: Variation in LOLE with System Annual Peak [1]

| System annual peak (MW) | Indices |
| --- | --- |
|  | Days/year | Years/day |
| 120 | 0.002005 | 498 |
| 130 | 0.04772 | 20.96 |
| 140 | 0.08687 | 11.51 |
| 150 | 0.1208 | 8.28 |
| 160 | 0.1506 | 6.64 |
| 170 | 1.895 | 0.53 |
| 180 | 3.447 | 0.29 |
| 190 | 4.837 | 0.21 |
| 200 | 6.083 | 0.16 |

The LOLE (days/year) is plotted on semi-log scale in Fig. U19.16.

Fig. U19.16: LOLE as a function of system annual peak load [1]

Obviously, we must add some capacity before we reach an annual peak demand of 200 MW. But at what peak demand level should that be done?

The answer to this question can be identified if we select a threshold risk level beyond which we will not allow. This is basically a management decision, but of course, all management decisions can be facilitated by quantitative analysis. We will forego such analysis here and instead arbitrarily select 0.15 days/year as the threshold risk level.

Assume:

- we have forecasted a 10% per year load growth,

- we have decided to add one 50 MW unit at a time, each with FOR=0.01, as the load grows, in order to ensure the system satisfies the identified threshold risk level.

The question is: when do we add the units?

To answer this question, we will repeat the analysis of Table U19.10, except for four different installed capacities: 200 MW, 250 MW, 300 MW, and 350 MW, corresponding to additional units of 0, 1, 2, and 3, respectively.

Table U19.11 summarizes the calculations. Fig. U19.17 illustrates the variation in LOLE with peak load for each case, together with vertical lines indicating the peak load value for each year.

The unit additions would need to be made in years 2, 4, and 6. The dotted line tracks the year-by-year risk variation.

This approach ensures that the stated reliability criteria are met; however, the other influence to the decision-making process is, as always, economic. Recall that we assumed that we would solve our capacity problem by adding capacity at increments of 50 MW at a time. It would be quite atypical if this were the only solution approach considered. For example, one might consider larger or smaller increments, or more or less reliable units (different FOR).

Different decisions would have different influence on the system risk; they would also have different present worth values. The influence on risk and present worth would need be weighed one against another in order to arrive a “good” decision.

Question:

Why would you want to perform this kind of calculation for a system in which generators are built by electricity market participants rather than a centralized vertically integrated utility company?

Table U19.11: LOLE Calculations for Example [1]

| System annual peak (MW) | LOLE (days/year) |
| --- | --- |
|  | 200 MW | 250 MW | 300 MW | 350 MW |
| 100 | 0.001210 | - | - | - |
| 120 | 0.002005 | - | - | - |
| 140 | 0.08687 | 0.001301 | - | - |
| 160 | 0.1506 | 0.002625 | - | - |
| 180 | 3.447 | 0.06858 | - | - |
| 200 | 6.083 | 0.1505 | 0.002996 | - |
| 220 | - | 2.058 | 0.03615 | - |
| 240 | - | 4.853 | 0.1361 | 0.002980 |
| 250 | - | 6.083 | 0.1800 | 0.004034 |
| 260 | - | - | 0.6610 | 0.01175 |
| 280 | - | - | 3.566 | 0.1075 |
| 300 | - | - | 6.082 | 0.2904 |
| 320 | - | - | - | 2.248 |
| 340 | - | - | - | 4.880 |
| 350 | - | - | - | 6.083 |

Fig. U19.17: Capacity planning example [1]

# U19.6	The effective load approach

Most of what we have seen in sections U19.1-U19.5 characterize the view taken by [1]. We now provide another view, based on [2].

## U19.6.1 Preliminary Definitions

Let’s characterize the load shape curve with t=g(d), as illustrated in Fig. U19.18. It is important to note that the load shape curve characterizes the (forecasted) future time period and is therefore a probabilistic characterization of the demand.

Fig. U19.18: Load shape t=g(d)

Here:

- d is the system load

- t is the number of time units in the interval T for which the load is greater than d and is most typically given in hours or days

- t=g(d) expresses the functional dependence of t on d

- T represents, most typically, a day, week, month, or year

The cumulative distribution function (cdf) introduced in Section U19.3 is given by

(U19.15)

One may also compute the total energy ET consumed in the period T as the area under the curve, i.e.,

(U19.16)

The average demand in the period T is obtained from

(U19.17)

Now let’s assume that the planned system generation capacity, i.e, the installed capacity, is CT, and that CT<dmax. This is an undesirable situation, since we will not be able to serve some demands, even when there is no capacity outage! Nonetheless, it serves well to understand the relation of the load duration curve to several useful indices. The situation is illustrated in Fig. U19.19.

Fig. U19.19: Illustration of Unserved Demand

Then, under the assumption that the given capacity CT is perfectly reliable, we may express three useful reliability indices:

- Loss of load expectation, LOLE: the number of time units that the load will exceed the capacity,

(U19.18)

- Loss of load probability, LOLP: the probability that the load will be interrupted during the time period T

(U19.19)

One may think that, given CT<dmax, then LOLP=1, i.e., the event “load interruption during T” is certain. The reason why it is not certain is because the load model is probabilistic. So LOLP is simply reflecting the uncertainty associated with demand, i.e., the demand may or may not exceed CT, according to FD(CT).

- Expected demand not served, EDNS: If the average (or expected) demand is given by (U19.17), then it follows that the expected demand not served would be:

(U19.20)

which would be the same area as in U19.19 when the ordinate is normalized to provide FD(d) instead of t. Reference [2]  provides a rigorous derivation for (U19.20).

- Expected energy not served, EENS: This is the total amount of time multiplied by the expected demand not served, i.e.,

(U19.21)

which is the area shown in Fig. U19.19.

## U19.6.2 Effective load

The notion of effective load is used to account for the unreliability of the generation, and it is essential for understanding the view taken by [2].

The basic idea is that the total system capacity is always CT, and the effect of capacity outages are accounted for by changing the load model in an appropriate fashion, and then the different indices are computed as given in (U19.18), (U19.19), and (U19.20).

A capacity outage of Ci is therefore modeled as an increase in the demand, not as a decrease in capacity!

We have already defined D as the random variable characterizing the demand. Now we define two more random variables:

- Dj is the random increase in load for outage of unit i.

- De is the random load accounting for outage of all units and represents the effective load.

Thus, the random variables D, De, and Dj are related according to:

(U19.21)

It is important to realize that, whereas Cj represents the capacity of unit j and is a deterministic value, Dj represents the increase in load corresponding to outage of unit j and is a random variable. The probability mass function (pmf) for Dj is assumed to be as given in Fig. U19.20, i.e., a two-state model. We denote the pmf for Dj as fDj(dj)

Fig. U19.20: Two state generator outage model

Recall from module U13 that the pdf of the sum of two random variables is the convolution of their individual pdfs. In addition, it is true that the cdf of two random variables can be found by convolving the cdf of one of them with the pdf (or pmf) of the other, that is, for random variables X and Y, with Z=X+Y, that

(U19.22)

Let’s consider the case for only one unit, i.e., from (U19.21),

(U19.23)

Then, by (U19.22), we have that:

(U19.24)

where the notation  indicates the cdf after the jth unit is convolved in. Under this notation, then, (U19.23) becomes

(U19.25)

and the general case for (U19.24) is:

(U19.26)

which expresses the equivalent load after the jth unit is convolved in.

Since fDj(dj) is discrete (i.e., a pmf), we may rewrite (U19.26) as

(U19.27)

From an intuitive perspective, (U19.27) is providing the convolution of the load shape  with the set of impulse functions comprising fDj(dj). When using a 2-state model for each generator, fDj(dj) is comprised of only 2 impulse functions, one at 0 and one at Cj. Recalling that the convolution of a function with an impulse function simply shifts and scales that function, (U19.27) can be expressed for the 2-state generator model as:

(U19.28)

So the cdf for the effective load following convolution with capacity outage pmf of the jth unit, is the sum of

- the original cdf, scaled by Aj and

- the original cdf, scaled by Uj and right-shifted by Cj.

Example: Fig. U19.21 illustrates the convolution process for a single unit C1=4 MW supplying a system having peak demand dmax=4 MW, with demand cdf given as in plot (a) based on a total time interval of T=1 year.

Fig. U19.21: Convolving in the first unit

Plots (c) and (d) represent the intermediate steps of the convolution where the original cdf  was scaled by A1=0.8 and U1=0.2, respectively, and right-shifted by 0 and C1=4, respectively. Note the effect of convolution is to spread the original cdf.

Plot (d) may raise some question since it appears that the constant part of the original cdf has been extended too far to the left. The reason for this apparent discrepancy is that all of the original cdf, in plot (a), was not shown. The complete cdf is illustrated in Fig. U19.22 below, which shows clearly that  for de<0, reflecting the fact that P(De>de)=1 for de<0.

Fig. U19.22: Complete cdf including values for de<0

Let’s consider that the “first” unit we just convolved in is actually the only unit. If that unit were perfectly reliable, then, because C1=4 and dmax=4, our system would never have loss of load. This would be the situation if we applied the ideas of Fig. U19.19 to Fig. U19.21, plot (a).

However, Fig. U19.21, plot (e) tells a different story. Fig. U19.23 applies the ideas of Fig. U19.19 to Fig. U19.21, plot (e) to show how the cdf on the equivalent load indicates that, for a total capacity of CT=4, we do in fact have some chance of losing load.

Fig. U19.23: Illustration of loss of load region

The desired indices are obtained from (U19.18), (U19.19), and (U19.20) as:

A LOLE of 0.2 years is 73 days, a very poor reliability level that reflects the fact we have only a single unit with a high FOR=0.2.

The LOLP is given by:

and the EDNS is given by:

which is just the shaded area in Fig. U19.23, most easily computed using the basic geometry of the figure, according to:

The EENS is given by

or T(EDNS=1(0.5)=0.5MW-years, or 8760(0.5)=4380MWhrs.

# U19.7	Four additional issues

A more extended treatment of generation adequacy evaluation would treat a number of additional issues. Here, we just point to these issues with a brief overview of each so that the interested reader may follow up on them as desired. The main issues are model uncertainty (U16.7.1), maintenance (U16.7.2), convolution techniques (U16.7.3), and frequency and duration approach (U16.7.4).

## U19.7.1	Model uncertainty

We have modeled uncertainty in our analysis of generation adequacy. However, we have assumed that our uncertainty models are precise, i.e, the unit FORs and the load forecast used to obtain the load duration curves are both perfectly accurate. The fact of the matter is that the unit FORs and the load forecast are estimates of the “true” parameters, and they will always be estimates no matter how much data is collected! Therefore, it is of interest to model uncertainty in the model parameters and then identify the influence of these uncertainties on the resulting adequacy indices.

One method of modeling parameter uncertainty is to represent each parameter with a numerical distribution. Then repeatedly draw values from each distribution, and calculate the reliability indices using those values. If the parameter values are drawn as a function of their probabilities, as indicated by the distribution, then the computed reliability indices will also form a distribution, from which we may compute their statistics, e.g., mean, variance, etc.

For example, if the peak load is normally distributed, then the distribution may be discretized, and each interval of the distribution can be assigned to an interval on (0,1) in proportion to its area under the normal curve. Then a random draw on (0,1), which is then converted to the peak load value through the assignment, will reflect the desired normal distribution. Figure U19.24 illustrates the process.

Fig. U19.24: Monte Carlo Simulation

This process is called Monte Carlo simulation (MCS) and is almost always an available option for computing reliability indices under parameter uncertainty. The advantage to MCS is that it is conceptually simple to implement. The disadvantage is that it is computationally intensive.

Load forecast uncertainty:

There are two basic methods. The first, well articulated in [1], is the most computational but the easiest to understand. The approach is to model the peak load using a discretized normal distribution, as shown in Fig. U19.24, where the mean of the distribution corresponds to the forecasted load.

Fig. U19.25: Modeling of load uncertainty [1]

The load shape curve is adjusted for each of the load values corresponding to the seven standard deviations from the mean       (-3, -2, -1, 0, 1, 2, 3), where 1 standard deviation is estimated based on the load forecasting program used and the amount of time over which the forecast is being done. A reasonable value could be 2%, for example.

Then the indices are computed for each different load shape and composite indices are computed as a weighted function of the individual indices, where the weights are the probabilities given in Fig. U19.25.

A second method is given in [1] but perhaps more thoroughly described in [2]. The basic idea is that a single cdf is constructed that reflects the uncertainty of the peak load forecast, using

(U19.29)

Once this cdf is obtained, the indices are computed using one of our standard approaches.

It is important to realize that modeling of uncertainty in load forecast always results in indices reflecting poorer reliability because the rate of increase of the indices is nonlinear with peak load, in that it is higher at higher load levels than at lower load levels.

FOR uncertainty:

References [1, 4] address inclusion of FOR uncertainty using a covariance matrix corresponding to the capacity outage table. The method is based on [5]. One important conclusion from this work is that although FOR uncertainty certainly affects the distribution of the reliability indices, it does not affect their expected values. This is in contrast to load forecast uncertainty.

## U19.7.2	Maintenance

The conceptually simplest method for including unit maintenance is through the capacity outage approach according to the following:

- Compute a “full” capacity outage table.

- Divide the year into Ny intervals and obtain a unique load shape cdf FDp(d) for each period p.

- For each interval p=1, Ny

  - Identify the units out on maintenance in this interval

  - Deconvolve each outaged unit from the capacity outage table to get a capacity outage table for period p, using the algorithm of Section U19.2.4. Denote the resulting capacity outage pmf as fYp(y).

  - Compute the LOLE for period p as (similar to (U19.14)):

(U19.30)

where Np is the total number of capacity outage states for period p and Ndays are the number of days in period p.

- The annual LOLE is then given as the sum of the LOLEp, i.e.,

(U19.31)

## U19.7.3	Convolution techniques

We have seen that convolution plays a major role in both the capacity table approach and the effective load approach. The convolution method illustrated for both approaches is called the recursive method. One drawback of this method is that it is quite computationally intensive and can require significant computer resources when it is used for systems having a large number of units and/or units with a large number of derated states.

As a result, there has been a great deal of research effort into developing faster convolution methods. This work has resulted in, in addition to the recursive method, the following methods [3]:

- Fourier transform [6]

- Method of cumulants [7]

- Segmentation method [8, 9, 10]

- Energy function method [3]

Of these, the method of cumulants is very fast, and the recursive method very is accurate. The segmentation method is said to achieve a good tradeoff between speed and accuracy. Note that Chanan Singh summarizes the method of cumulants in his notes [12].

## U19.7.4	Frequency and duration approach

The methods presented in this module so far provide the ability to compute LOLP, LOLE, EDNS, and EENS, but they do not provide the ability to compute

- Frequency of occurrence of an insufficient capacity condition

- The duration for which an insufficient capacity condition is likely to exist.

A competing method which provides these latter quantities goes, quite naturally, under the name of the frequency and duration (F&D) approach. The F&D approach is based on state space diagrams and Markov models. We touched on this at the end of Section U19.2.1 above by showing that we may represent a 2 generator system via a Markov model and then compute state probabilities, frequencies, and durations for each of the states.

The underlying steps for the F&D approach, outlined in chapter 10 of [11], are:

- Develop the Markov model and corresponding state transition matrix, A for the system.

- Use the state transition matrix to solve for the long-run probabilities from 0=pA and ∑pj=1 (note that we have dropped the subscript ( for brevity, but it should be understood that all probabilities in this section are long-run probabilities).

- Evaluate the frequency of encountering the individual states from (U16.31), repeated here for convenience:

(U19.32)

which can be expressed as:

fj=pj,([total rate of departure from state j]

- Evaluate the mean duration of each state, i.e., the mean time of residing in each state, from (U16.33), repeated here for convenience:

(U19.33)

(Note that [11] uses mj to denote the duration for state j and uses Tj to denote the cycle time for state j, which is the reciprocal of the state j frequency fj. One should carefully distinguish between the cycle time and the mean duration.

- The cycle time is the mean time between entering a given state to next entering that same state.

- The duration is the mean time of remaining in a given state.)

- Identify the states corresponding to failure, lumped into a cumulative state denoted as J.

- Compute the cumulative probability of the failure states pJ as the sum of the individual state probabilities:

(U19.34)

- Compute the cumulative frequency fJ of the failure states (see section U16.8.2) as the total of the frequencies leaving a failure state j for an non-failure state k:

(U19.35)

Because (see (U16.29)) fjk=λjk pj,(, (U19.35) can be expressed as

(U19.36)

- Compute the cumulative duration for the failure states, as:

(U19.37)

The above approach is quite convenient for a system of just a very few states, and it is important for our purposes because it lays out the underlying principles on which the F&D is based.

However, for a large system, the above approach is not very useful because of step 1 where we must develop the Markov model. This difficulty is circumvented by building the capacity outage table using recursive relations for the capacity outage (e.g. state) probabilities together with additional recursive relations for state transitions and state frequencies [1, 2, 4, 11].

# References

R. Billinton and R. Allan, “Reliability Evaluation of Power Systems, 2nd edition, Plenum Press, 1996.

R. Sullivan, “Power System Planning,” McGraw Hill, 1977.

X. Wang and J. McDonald, “Modern Power System Planning,” McGraw Hill, 1994.

J. Endrenyi, “Reliability modeling in electric power systems,” Wiley and Sons, New York, 1978.

A. Patton and A. Stasinos, “Variance and approximate confidence limits on LOLP for a single-area system,” IEEE Trans. on Power Apparatus and Systems, Vol. 94. pp. 1326-1336, July/August 1975.

N. Rau and K. Schenk, “Application of Fourier Methods for the Evaluation of Capacity Outage Probabilities,” IEEE PES 1979 Winter Power Meeting, paper A-79-103-3.

N. Rau, P. Toy, and K. Schenk, “Expected energy production costs by the method of moments,” IEEE Trans. on Power Apparatus and Systems, vol. PAS-99, no. 5, pp 1908-1917, Sep/Oct., 1980.

K. F. Schenk, R. B. Misra, S. Vassos and W. Wen, ‘A New Method for the Evaluation of Expected Energy Generation and Loss of Load Probability’, IEEE Transaction on Power Apparatus and Systems, Vol. PAS-103, No. 2, Feb. 1984.

Y. Dai, J. McCalley, and V. Vittal, “Annual Risk Assessment for Thermal Overload,” Proceedings of the 1998 American Power Conference, Chicago, Illinios, April, 1998.

Y. Dai, “…,” Ph.D. Dissertation, Iowa State University, 1999.

R. Billinton and R. Allan, “Reliability evaluation of engineering systems,” 2nd edition, Plenum Press, New York, 1992.

C. Singh, “Electric Power System Reliability – Course Notes.”

# Text boxes

0

max



)



(

d

T

dλ

(

g

E